## Slide 1: ECEN 667 Power System Stability
Lecture 10: Synchronous Machine Models,
Exciter Models
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University, overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 4
Homework 3 is posted, due on Thursday Oct 5
Midterm exam is Oct 17 in class; closed book, closed notes, one 8.5 by 11 inch hand written notesheet allowed; calculators allowed

## Slide 3: GENSAL Block Diagram
A quadratic saturation function is used. For initialization it only impacts the Efd value

## Slide 4: GENSAL Example
Assume same system as before with same common generator parameters: H=3.0, D=0, Ra = 0, Xd = 2.1, Xq = 2.0, X'd = 0.3, X"d=X"q=0.2, Xl = 0.13, T'do = 7.0, T"do = 0.07, T"qo =0.07, S(1.0) =0, and S(1.2) = 0.
Same terminal conditions as before
    Current of 1.0-j0.3286 and generator terminal voltage of 1.072+j0.22 = 1.0946 11.59 
Use same equation to get initial d
Same delta as with the other models

## Slide 5: GENSAL Example
Then as before And

## Slide 6: GENSAL Example
Giving the initial fluxes (with w = 1.0)
To get the remaining variables set the differential equations equal to zero, e.g.,
Solving the d-axis requires solving two linear equations for two unknowns

## Slide 7: GENSAL Example
0.4118
0.5882
0.17
Id=0.9909
d”=1.031
1.8
Eq’=1.1298
d’=0.9614
3.460
Efd = 1.1298+1.8*0.991=2.912

## Slide 8: Comparison Between Gensal and Flux Decay

## Slide 9: Nonlinear Magnetic Circuits
Nonlinear magnetic models are needed because magnetic materials tend to saturate; that is, increasingly large amounts of current are needed to increase the flux density
Linear

## Slide 10
Saturation
The flux density (B) determines when a material saturates; measured in Tesla (T)

## Slide 11: Relative Magnetic Strength Levels
Earth’s magnetic field is between 30 and 70 mT (0.3 to 0.7 gauss)
A refrigerator magnet might have 0.005 T
A commercial neodymium magnet might be 1 T
A magnetic resonance imaging (MRI) machine would be between 1 and 3 T
Strong lab magnets can be 10 T
Frogs can be levitated at 16 T (see www.ru.nl/hfml/research/levitation/diamagnetic
A neutron star can have 1 to 100 MT!

## Slide 12: Magnetic Saturation and Hysteresis
The below image shows the saturation curves for various materials
Image Source: en.wikipedia.org/wiki/Saturation_(magnetic)
Magnetization curves of 9 ferromagnetic materials, showing saturation. 1.Sheet steel, 2.Silicon steel, 3.Cast steel, 4.Tungsten steel, 5.Magnet steel, 6.Cast iron, 7.Nickel, 8.Cobalt, 9.Magnetite; highest saturation materials can get to around 2.2 or 2.3T
H is proportional to current

## Slide 13: Magnetic Saturation and Hysteresis
Magnetic materials also exhibit hysteresis, so there is some residual magnetism when the current goes to zero; design goal is to reduce the area enclosed by the hysteresis loop
Image source: www.nde-ed.org/EducationResources/CommunityCollege/MagParticle/Graphics/BHCurve.gif
To minimize the amount of magnetic material, and hence cost and weight, electric machines are designed to operate close to saturation

## Slide 14: Saturation Models
Many different models exist to represent saturation
  There is a tradeoff between accuracy and complexity
Book presents the details of fully considering saturation in Section 3.5
One simple approach is to replace
With

## Slide 15: Saturation Models
In steady-state this becomes
Hence saturation increases the required Efd to get a desired flux
Saturation is usually modeled using a quadratic function, with the value of Se specified at two points (often at 1.0 flux and 1.2 flux)
A and B are determined from the two data points

## Slide 16: Saturation Example
If Se = 0.1 when the flux is 1.0 and 0.5 when the flux is 1.2, what are the values of A and B using the

## Slide 17: Saturation Example: Selection of A
When selecting which of the two values of A to use, we do not want the minimum to be between the two specified values. That is Se(1.0) and Se(1.2).

## Slide 18: Implementing Saturation Models
When implementing saturation models in code, it is important to recognize that the function is meant to be positive, so negative values are not allowed
In large cases one is almost guaranteed to have special cases, sometimes caused by user typos
  What to do if Se(1.2) < Se(1.0)?
  What to do if Se(1.0) = 0 and Se(1.2) <> 0
  What to do if Se(1.0) = Se(1.2) <> 0
Exponential saturation models have also been used

## Slide 19: GENSAL Example with Saturation
Once E'q has been determined, the initial field current (and hence field voltage) are easily determined by recognizing in steady-state the E'q is zero
Saved as case B4_GENSAL_SAT
Saturation coefficients were determined from the two initial values

## Slide 20: GENROU
The GENROU model has been widely used to model round rotor machines
Saturation is assumed to occur on both the d-axis and the q-axis, making initialization slightly more difficult

## Slide 21: GENROU Block Diagram
The d-axis is similar to that of the GENSAL; the q-axis is now similar to the d-axis. Note that saturation now affects both axes.

## Slide 22: GENROU Initialization
Because saturation impacts both axes, the simple approach will no longer work
Key insight for determining initial d is that the magnitude of the saturation depends upon the magnitude of ", which is independent of d
Solving for d requires an iterative approach; first get a guess of d using 3.229 from the book
This point is crucial!

## Slide 23: GENROU Initialization
Then solve five nonlinear equations for five unknowns
  The five unknowns are d, E'q, E'd,  'q, and  'd
Five equations come from the terminal power flow constraints (which allow us to define d " and q" as a function of the power flow voltage, current and d) and from the differential equations initially set to zero
  The d " and q" block diagram constraints
  Two differential equations for the q-axis, one for the d-axis (the other equation is used to set the field voltage
Values can be determined using Newton’s method, which is needed for the nonlinear case with saturation

## Slide 24: GENROU Initialization
Use dq transform to express terminal current as
Get expressions for  "q and  "d in terms of the initial terminal voltage and d
  Use dq transform to express terminal voltage as
  Then from
Recall Xd"=Xq"=X" and w=1 (in steady-state)
Expressing complex equation as two real equations
These values will change during the iteration as d changes

## Slide 25: GENROU Initialization Example
Extend the two-axis example
  For two-axis assume H = 3.0 per unit-seconds, Rs=0, Xd = 2.1, Xq = 2.0, X'd= 0.3, X'q = 0.5, T'do = 7.0, T'qo = 0.75 per unit using the 100 MVA base.
  For subtransient fields assume X"d=X"q=0.28, Xl = 0.13, T"do = 0.073, T"qo =0.07
  for comparison we'll initially assume no saturation
From two-axis get a guess of d

## Slide 26: GENROU Initialization Example
And the network current and voltage in dq reference
Which gives initial subtransient fluxes (with Rs=0),

## Slide 27: GENROU Initialization Example
Without saturation this is the exact solution
  Initial values are: d = 52.1, E'q=1.1298, E'd=0.533,  'q =0.6645, and  'd=0.9614
Efd=2.9133
Saved as case B4_GENROU_NoSat

## Slide 28: Two-Axis versus GENROU Response
Figure compares rotor angle for bus 3 fault, cleared at t=1.1 seconds

## Slide 29: GENROU with Saturation
Nonlinear approach is needed in common situation in which there is saturation
Assume previous GENROU model with S(1.0) = 0.05, and S(1.2) = 0.2.
  Initial values are: d = 49.2, E'q=1.1591, E'd=0.4646,  'q =0.6146, and  'd=0.9940
Efd=3.2186
Saved as case B4_GENROU_Sat

## Slide 30: Two-Axis versus GENROU Response

## Slide 31: GENTPF and GENTPJ Models
These models were introduced into PSLF in 2009 to provide a better match between simulated and actual system results for salient pole machines
  Desire was to duplicate functionality from old BPA TS code
  Allows for subtransient saliency (X"d <> X"q)
  Can also be used with round rotor, replacing GENSAL and GENROU
Useful reference is available at below link; includes all the equations, and saturation details
https://www.wecc.biz/Reliability/gentpj-typej-definition.pdf

## Slide 32: GENSAL Results
Image source :https://www.wecc.biz/library/WECC%20Documents/Documents%20for %20Generators/Generator%20Testing%20Program/gentpj%20and%20gensal%20morel.pdf
Chief Joseph
disturbance playback
GENSAL
BLUE = MODEL
RED = ACTUAL

## Slide 33: GENTPJ Results
Chief Joseph
disturbance playback
GENTPJ
BLUE = MODEL
RED = ACTUAL

## Slide 34: GENTPF and GENTPJ Models
GENTPF/J d-axis block diagram
GENTPJ allows saturation function to include a component that depends on the stator current
Se = 1 + fsat( ag + Kis*It)
Most of WECC machine models are now GENTPF or GENTPJ
If nonzero, Kis typically ranges from 0.02 to 0.12

## Slide 35: Theoretical Justification for GENTPF and GENTPJ
In the GENROU and GENSAL models saturation shows up purely as an additive term of Eq’ and Ed’
  Saturation does not come into play in the network interface equations and thus with the assumption of Xq”=Xd” a simple circuit model can be used
The advantage of the GENTPF/J models is saturation really affects the entire model, and in this model it is applied to all the inductance terms simultaneously
  This complicates the network boundary equations, but since these models are designed for Xq”≠ Xd” there is no increase in complexity

## Slide 36: GENROU/GENTPJ Comparison
Easy Paper Suggestion (Done by Birchfield in 2017 GM)!

## Slide 37: GenRou, GenTPF, GenTPJ
Figure compares gen 4 reactive power output for the 0.1 second fault

## Slide 38
Voltage and Speed Control

## Slide 39: Exciters, Including AVR
Exciters are used to control the synchronous machine field voltage and current
  Usually modeled with automatic voltage regulator included
A useful reference is IEEE Std 421.5-2016
  Just updated from the 2005 edition!
  Covers the major types of exciters used in transient stability
  Continuation of standard designs started with "Computer Representation of Excitation Systems," IEEE Trans. Power App. and Syst., vol. pas-87, pp. 1460-1464, June 1968
Another reference is P. Kundur, Power System Stability and Control, EPRI, McGraw-Hill, 1994
  Exciters are covered in Chapter 8 as are block diagram basics

## Slide 40: Functional Block Diagram
Image source: Fig 8.1 of Kundur, Power System Stability and Control

## Slide 41: Types of Exciters
None, which would be the case for a permanent magnet generator
  primarily used with wind turbines with ac-dc-ac converters
DC: Utilize a dc generator as the source of the field voltage through slip rings
AC: Use an ac generator on the generator shaft, with output rectified to produce the dc field voltage; brushless with a rotating rectifier system
Static: Exciter is static, with field current supplied through slip rings