## Slide 1: ECEN 667 Power System Stability
Lecture 16: Transient Stability Solutions
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University, overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 7
Homework 5 is assigned today, due on Oct 31

## Slide 3: Adding Network Equations
Previous slides with the network equations embedded in the differential equations were a special case
In general with the explicit approach we'll be alternating between solving the differential equations and solving the algebraic equations
Voltages and currents in the network reference frame can be expressed using either polar or rectangular coordinates
In rectangular with the book's notation we have

## Slide 4: Adding Network Equations
Network equations will be written as Y V- I(x,V) = 0
  Here Y is as from the power flow, except augmented to include the impact of the generator's internal impedance
  Constant impedance loads are also embedded in Y; non-constant impedance loads are included in I(x,V)
If I is independent of V then this can be solved directly: V = Y-1I(x)
In general an iterative solution is required, which we'll cover shortly, but initially we'll go with just the direct solution

## Slide 5: Two Bus Example, Except with No Infinite Bus
To introduce the inclusion of the network equations, the previous example is extended by replacing the infinite bus at bus 2 with a classical model with Xd2'=0.2, H2=6.0
PowerWorld Case B2_CLS_2Gen

## Slide 6: Bus Admittance Matrix
The network admittance matrix is
This is augmented to represent the Norton admittances associated with the generator models (Xd1'=0.3, Xd2'=0.2)
In PowerWorld you can see this matrix by selecting Transient Stability, States/Manual Control, Transient Stability Ybus

## Slide 7: Current Vector
For the classical model the Norton currents are given by
The initial values of the currents come from the power flow solution
As the states change (di for the classical model), the Norton current injections also change

## Slide 8: B2_CLS_Gen Initial Values
The internal voltage for generator 1 is as before
We likewise solve for the generator 2 internal voltage
The Norton current injections are then
Keep in mind the Norton current injections are not the current out of the generator
0.4179 radians
0.2108 radians

## Slide 9: B2_CLS_Gen Initial Values
To check the values, solve for the voltages, with the values matching the power flow values

## Slide 10: Swing Equations
With the network constraints modeled, the swing equations are modified to represent the electrical power in terms of the generator's state and current values
Then swing equation is then
IDi+jlQi is the current being injected into the network by the generator

## Slide 11: Two Bus, Two Generator Differential Equations
The differential equations for the two generators are
In this example PM1 = 1 and PM2 = -1

## Slide 12: PowerWorld GENCLS Initial States

## Slide 13: Solution at t=0.02
Usually a time step begins by solving the differential equations. However, in the case of an event, such as the solid fault at the terminal of bus 1, the network equations need to be first solved
Solid faults can be simulated by adding a large shunt at the fault location
  Amount is somewhat arbitrary, it just needs to be large enough to drive the faulted bus voltage to zero
With Euler's the solution after the first time step is found by first solving the differential equations, then resolving the network equations

## Slide 14: Solution at t=0.02
Using Yfault = -j1000, the fault-on conditions become

## Slide 15: Solution at t=0.02
Then the differential equations are evaluated, using the new voltages and currents
  These impact the calculation of PEi with PE1=0, PE2=0
If solving with Euler's this is the final state value; using these state values the network equations are resolved, with the solution the same here since the d's didn't vary

## Slide 16: PowerWorld GENCLS at t=0.02

## Slide 17: Solution Values Using Euler's
The below table gives the results using Dt = 0.02 for the beginning time steps
Time (Sec) | Gen 1 Rotor Angle | Gen 1 Speed (Hz) | Gen 2 Rotor Angle | Gen2 Speed (Hz)
0 | 23.9462 | 60 | -12.0829 | 60
0.02 | 23.9462 | 60.2 | -12.0829 | 59.9
0.04 | 25.3862 | 60.4 | -12.8029 | 59.8
0.06 | 28.2662 | 60.6 | -14.2429 | 59.7
0.08 | 32.5862 | 60.8 | -16.4029 | 59.6
0.1 | 38.3462 | 61 | -19.2829 | 59.5
0.1 | 38.3462 | 61 | -19.2829 | 59.5
0.12 | 45.5462 | 60.9128 | -22.8829 | 59.5436
0.14 | 52.1185 | 60.7966 | -26.169 | 59.6017
0.16 | 57.8541 | 60.6637 | -29.0368 | 59.6682
0.18 | 62.6325 | 60.5241 | -31.426 | 59.7379
0.2 | 66.4064 | 60.385 | -33.3129 | 59.8075
0.22 | 69.1782 | 60.2498 | -34.6988 | 59.8751
0.24 | 70.9771 | 60.1197 | -35.5982 | 59.9401
0.26 | 71.8392 | 59.9938 | -36.0292 | 60.0031
0.28 | 71.7949 | 59.8702 | -36.0071 | 60.0649

## Slide 18: Solution at t=0.02 with RK2
With RK2 the first part of the time step is the same as Euler's, that is solving the network equations with
Then calculate k2 and get a final value for x(t+Dt)
Finally solve the network equations using the final value for x(t+Dt)

## Slide 19: Solution at t=0.02 with RK2
From the first half of the time step
Then

## Slide 20: Solution at t=0.02 with RK2
The new values for the Norton currents are

## Slide 21: Solution Values Using RK2
The below table gives the results using Dt = 0.02 for the beginning time steps
Time (Sec) | Gen 1 Rotor Angle | Gen 1 Speed (Hz) | Gen 2 Rotor Angle | Gen2 Speed (Hz)
0 | 23.9462 | 60 | -12.0829 | 60
0.02 | 24.6662 | 60.2 | -12.4429 | 59.9
0.04 | 26.8262 | 60.4 | -13.5229 | 59.8
0.06 | 30.4262 | 60.6 | -15.3175 | 59.7008
0.08 | 35.4662 | 60.8 | -17.8321 | 59.6008
0.1 | 41.9462 | 61 | -21.0667 | 59.5008
0.1 | 41.9462 | 61 | -21.0667 | 59.5008
0.12 | 48.7754 | 60.8852 | -24.4759 | 59.5581
0.14 | 54.697 | 60.7538 | -27.4312 | 59.6239
0.16 | 59.6315 | 60.6153 | -29.8931 | 59.6931
0.18 | 63.558 | 60.4763 | -31.8509 | 59.7626
0.2 | 66.4888 | 60.3399 | -33.3109 | 59.8308
0.22 | 68.4501 | 60.2071 | -34.286 | 59.8972
0.24 | 69.4669 | 60.077 | -34.789 | 59.9623
0.26 | 69.5548 | 59.9481 | -34.8275 | 60.0267
0.28 | 68.7151 | 59.8183 | -34.4022 | 60.0916

## Slide 22: Angle Reference
The initial angles are given by the angles from the power flow, which are based on the slack bus's angle
As presented the transient stability angles are with respect to a synchronous reference frame
  Sometimes this is fine, such as for either shorter studies, or ones in which there is little speed variation
  Oftentimes this is not best since the when the frequencies are not nominal, the angles shift from the reference frame
Other reference frames can be used, such as with respect to a particular generator's value, which mimics the power flow approach; the selected reference has no impact on the solution

## Slide 23: Subtransient Models
The Norton current injection approach is what is commonly used with subtransient models in industry
If subtransient saliency is neglected (as is the case with GENROU and GENSAL in which X"d=X"q) then the current injection is
  Subtransient saliency can be handled with this approach, but it is more involved (see Arrillaga, Computer Analysis of Power Systems, section 6.6.3)

## Slide 24: Subtransient Models
Note, the values here are on the dq reference frame
We can now extend the approach introduced for the classical machine model to subtransient models
Initialization is as before, which gives the d's and other state values
Each time step is as before, except we use the d's for each generator to transfer values between the network reference frame and each machine's dq reference frame
  The currents provide the coupling

## Slide 25: Two Bus Example with Two GENROU Machine Models
Use the same system as before, except with we'll model both generators using GENROUs
  For simplicity we'll make both generators identical except set H1=3, H2=6; other values are Xd=2.1, Xq=0.5, X'd=0.2, X'q=0.5, X"q=X"d=0.18, Xl=0.15, T'do = 7.0, T'qo=0.75, T"do=0.035, T"qo=0.05; no saturation
  With no saturation the value of the d's are determined (as per Lecture 11) by solving
  Hence for generator 1

## Slide 26: GENROU Block Diagram
E'q
E'd

## Slide 27: Two Bus Example with Two GENROU Machine Models
Using the approach from Lecture 11 the initial state vector is
Note that this is a salient pole machine with X'q=Xq; hence E'd will always be zero
The initial currents in the dq reference frame are Id1=0.7872, Iq1=0.6988, Id2=0.2314, Iq2=-1.0269
Initial values of "q1= -0.2236, and "d1 = 1.179

## Slide 28: PowerWorld GENROU Initial States

## Slide 29: Solving with Euler's
We'll again solve with Euler's, except with Dt set now to 0.01 seconds (because now we have a subtransient model with faster dynamics)
  We'll also clear the fault at t=0.05 seconds
For the more accurate subtransient models the swing equation is written in terms of the torques
Other equations are solved based upon the block diagram

## Slide 30: Norton Equivalent Current Injections
The initial Norton equivalent current injections on the dq base for each machine are
Recall the dq values are on the machine's reference frame and the DQ values are on the system reference
frame

## Slide 31: Moving between DQ and dq
Recall
And
The currents provide the key coupling between the two reference
frames

## Slide 32: Bus Admittance Matrix
The bus admittance matrix is as from before for the classical models, except the diagonal elements are augmented using

## Slide 33: Algebraic Solution Verification
To check the values solve (in the network reference frame)

## Slide 34: Results
The below graph shows the results for four seconds of simulation, using Euler's with Dt=0.01 seconds
PowerWorld case is
B2_GENROU_2GEN_EULER

## Slide 35: Results for Longer Time
Simulating out 10 seconds indicates an unstable solution, both using Euler's and RK2 with Dt=0.005, so it is really unstable!
Euler's with Dt=0.01
RK2 with Dt=0.005

## Slide 36: Adding More Models
In this situation the case is unstable because we have not modeled exciters
To each generator add an EXST1 with TR=0, TC=TB=0, Kf=0, KA=100, TA=0.1
  This just adds one differential equation per generator

## Slide 37: Two Bus, Two Gen With Exciters
Below are the initial values for this case from PowerWorld
Case is B2_GENROU_2GEN_EXCITER
Because of the zero values the other differential equations for the exciters are included but treated as ignored

## Slide 38: Viewing the States
PowerWorld allows one to single-step through a solution, showing the f(x) and the K1 values
  This is mostly used for education or model debugging
Derivatives shown are evaluated at the end of the time step

## Slide 39: Two Bus Results with Exciters
Below graph shows the angles with Dt=0.01 and a fault clearing at t=0.05 using Euler's
  With the addition of the exciters case is now stable

## Slide 40: Constant Impedance Loads
The simplest approach for modeling the loads is to treat them as constant impedances, embedding them in the bus admittance matrix
  Only impact the Ybus diagonals
The admittances are set based upon their power flow values, scaled by the inverse of the square of the power flow bus voltage
In PowerWorld the default load model is specified on Transient Stability, Options, Power System Model

## Slide 41: Example 7.4 Case (WSCC 9 Bus)
PowerWorld Case Example_7_4 duplicates the example 7.4 case from the book, with the exception of using different generator models

## Slide 42: Nonlinear Network Equations
With constant impedance loads the network equations can usually be written with I independent of V, then they can be solved directly (as we've been doing)
In general this is not the case, with constant power loads one common example
Hence a nonlinear solution with Newton's method is used
We'll generalize the dependence on the algebraic variables, replacing V by y since they may include other values beyond just the bus voltages

## Slide 43: Nonlinear Network Equations
Just like in the power flow, the complex equations are rewritten, here as a real current and a reactive current YV – I(x,y) = 0
The values for bus i are
For each bus we add two new variables and two new equations
If an infinite bus is modeled then its variables and equations are omitted since its voltage is fixed
This is a rectangular formulation; we also could have written the equations in polar form

## Slide 44: Nonlinear Network Equations
The network variables and equations are then

## Slide 45: Nonlinear Network Equation Newton Solution

## Slide 46: Network Equation Jacobian Matrix
The most computationally intensive part of the algorithm is determining and factoring the Jacobian matrix, J(y)

## Slide 47: Network Jacobian Matrix
The Jacobian matrix can be stored and computed using a 2 by 2 block matrix structure
The portion of the 2 by 2 entries just from the Ybus are
The major source of the current vector voltage sensitivity comes from non-constant impedance loads; also dc transmission lines
The "hat" was added to the g functions to
indicate it is just the portion from the Ybus

## Slide 48: Example: Constant Current and Constant Power Load
As an example, assume the load at bus k is represented with a ZIP model
The constant impedance portion is embedded in the Ybus
Usually solved in per unit on network MVA base
The base load values are set from the power flow

## Slide 49: Example: Constant Current and Constant Power Load
The current is then
Multiply the numerator and denominator by VDK+jVQK to write as the real current and the reactive current

## Slide 50: Example: Constant Current and Constant Power Load
The Jacobian entries are then found by differentiating with respect to VDK and VQK
  Only affect the 2 by 2 block diagonal values
Usually constant current and constant power models are replaced by a constant impedance model if the voltage goes too low, like during a fault