## Slide 1: ECEN 667 Power System Stability
Lecture 24:Stabilizer Design, Measurement Based Modal Analysis
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University, overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 9
Homework 7 is posted; due on Thursday Nov 30
Final is as per TAMU schedule. That is, Friday Dec 8 from 3 to 5pm

## Slide 3: Eastern Interconnect Frequency Distribution
Results Provided by Ogbonnaya Bassey using FNET Data

## Slide 4: Stabilizer Design
The following slides give an example of stabilizer design using the below single-input power system stabilizer (type PSS1A from IEEE Std. 421-5)
  We already considered the theory in lecture 22
  The PSS1A is very similar to the IEEEST Stabilizer and STAB1
Image Source: IEEE Std 421.5-2016

## Slide 5: Stabilizer References
Key papers on the example approach are
  E. V. Larsen and D. A. Swann, "Applying Power System Stabilizers Part I: General Concepts," in IEEE Transactions on Power Apparatus and Systems, vol.100, no. 6, pp. 3017-3024, June 1981.
  E. V. Larsen and D. A. Swann, "Applying Power System Stabilizers Part II: Performance Objectives and Tuning Concepts," in IEEE Transactions on Power Apparatus and Systems, vol.100, no. 6, pp. 3025-3033, June 1981.
  E. V. Larsen and D. A. Swann, "Applying Power System Stabilizers Part III: Practical Considerations," in IEEE Transactions on Power Apparatus and Systems, vol.100, no. 6, pp. 3034-3046, June 1981.
  Shin, Jeonghoon & Nam, Su-Chul & Lee, Jae-Gul & Baek, Seung-Mook & Choy, Young-Do & Kim, Tae-Kyun. (2010). A Practical Power System Stabilizer Tuning Method and its Verification in Field Test. Journal of Electrical Engineering and Technology. 5. 400-406.

## Slide 6: Stabilizer Design
As noted by Larsen, the basic function of stabilizers is to modulate the generator excitation to damp generator oscillations in frequency range of about 0.2 to 2.5 Hz
  This requires adding a torque that is in phase with the speed variation; this requires compensating for the gain and phase characteristics of the excitation system, generator, and power system
The stabilizer input is typically shaft speed
Image Source: Figure 1 from Larsen, 1981, Part 1

## Slide 7: Stabilizer Design
T6 is used to represent measurement delay; it is usually zero (ignoring the delay) or a small value (< 0.02 sec)
The washout filter removes low frequencies; T5 is usually several seconds (with an average of say 5)
  Some guidelines say less than ten seconds to quickly remove the low frequency component
  Some stabilizer inputs include two washout filters
Image Source: IEEE Std 421.5-2016

## Slide 8: Example Washout Filter Values
With T5= 10 at 0.1 Hz the gain is 0.987; with T5= 1 at 0.1 Hz the gain is 0.53
Graph plots the equivalent of T5 for an example actual system

## Slide 9: Stabilizer Design
The Torsional filter is a low pass filter to attenuate the torsional mode frequency
  We will ignore it here
Key parameters to be tuned at the gain, Ks, and the time constants on the two lead-lag blocks (to provide the phase compensation)
  We’ll assume T1=T3 and T2=T4

## Slide 10: Stabilizer Design Phase Compensation
Goal is to move the eigenvalues further into the left-half plane
Initial direction the eigenvalues move as the stabilizer gain is increased from zero depends on the phase at the oscillatory frequency
  If the phase is close to zero, the real component changes significantly but not the imaginary component
  If the phase is around -45 then both change about equally
  If the phase is close to -90 then there is little change in the real component but a large change in the imaginary component

## Slide 11: Stabilizer Design Tuning Criteria
Theoretic tuning criteria:
  Compensated phase should pass -90o after 3.5 Hz
  The compensated phase at the oscillatory frequency should be in the range of [-45o, 0o], preferably around -20o
  Ratio (T1T3)/(T2T4) at high frequencies should not be too large
A peak phase lead provided by the compensator occurs at the center frequency
  The peak phase lead increases as ratio T1/T2 increases
A practical method is:
  Select a reasonable ratio T1/T2; select T1 such that the center frequency is around the oscillatory frequency without the PSS

## Slide 12: Example T1 and T2 Values
The average T1 value is about 0.25 seconds and T2 is 0.1 seconds, but most T2 values are less than 0.05; the average T1/T2 ratio is 6.3

## Slide 13: Stabilizer Design Tuning Criteria
Eigenvalues moves as Ks increases
A practical method is to find KINST, then set KOPT as about 1/3 or ¼ this value
  KOPT is where the damping is maximized
  KINST is the gain at which sustained oscillations or an instability occur

## Slide 14: Example with 42 Bus System
A three-phase fault is applied to the middle of the 345 kV transmission line between Prairie (bus 22) and Hawk (bus 3) with both ends opened at 0.05 seconds

## Slide 15: Step 1: Decide Generators to Tune and Frequency
Generator speeds and rotor angles are observed to have a poorly damped oscillation around 0.6 Hz.

## Slide 16: Step 1: Decide Generators to Tune and Frequency
In addition to interpreting from those plots, a modal analysis tool could assist in finding the oscillation information
We are going to tune PSS1A models for all generators using the same parameters (doing them individually would be better by more time consuming)

## Slide 17: Step 2: Phase Compensation
Select a ratio of T1/T2 to be ten
Select T1 so fc is 0.6 Hz

## Slide 18: Step 3: Gain Tuning
Find the KINST, which is the gain at which sustained oscillations or an instability occur
This occurs at about 9 for the gain
Easiest to see the oscillations just by plotting the stabilizer output signal

## Slide 19: Step 4: Testing on Original System
With gain set to 3
Better tuning would be possible with customizing for the individual generators

## Slide 20: Dual Input Stabilizers
Images Source: IEEE Std 421.5-2016
PSS3C
PSS2C
The PSS2C supersedes the PSS2B, adding an additional lead-lag block and bypass logic

## Slide 21: TSGC 2000 Bus VPM Example

## Slide 22: TSGC 2000 Bus Example
Results obtained with a time period from 1 to 20 seconds, sampling at 4 Hz
Most significant frequencies are at 0.225 and 0.328 Hz

## Slide 23: Mode Observability, Shape, Controllability and Participation Factors
In addition to frequency and damping, there are several other mode characteristics
Observability tells how much of the mode is in a signal, hence it is associated with a particular signal
Mode Shape is a complex number that tells the magnitude and phase angle of the mode in the signal (hence it quantifies observability)
Controllability specifies the amount by which a mode can be damped by a particular controller
Participation facts is used to quantify how much damping can be provided for a mode by a PSS

## Slide 24: Determining Modal Shape Example
Example uses the four generator system shown below in which the generators are represented by a combination of GENCLS and GENROU. The contingency is a self-clearing fault at bus 1
  The generator speeds (the signals) are as shown in the right figure
Case is saved as B4_Modes

## Slide 25: Determining Modal Shape Example
Example uses the multi-signal VPM to determine the key modes in the signals
  Four modes were identified, though the key ones were at 1.22, 1.60 and 2.76 Hz

## Slide 26: Determining Modal Shape Example
Information about the mode shape is available for each signal; the mode content in each signal can also be isolated
Graph shows original and the reproduced signal

## Slide 27: Determining Modal Shape Example
Graph shows the contribution provided by each mode in the generator 1 speed signal
Reproduced without 1.22 and 2.76 Hz
Reproduced without 2.76 Hz

## Slide 28: Modes Shape by Generator (for Speed)
The table shows the contributions by mode for the different generator speed signals
Mode (Hz) | Gen 1 | Gen 2 | Gen 3 | Gen 4
0.244 | 0.07 | 0.082 | 0.039 | 0.066
1.22 | 1.567 | 1.494 | 0.097 | 0.01
1.6 | 2.367 | 2.203 | 2.953 | 1.639
2.76 | 0.174 | 0.378 | 0.927 | 4.913
Image on the right shows the Gen 4 2.76 Hz mode; note it is highly damped

## Slide 29: Modes Depend on the Signals!
The below image shows the bus voltages for the previous system, with some (poorly tuned) exciters
  Response includes a significant 0.664 Hz mode from the gen 4 exciter (which can be seen in its SMIB eigenvalues)

## Slide 30: Inter-Area Modes in the WECC
The dominant inter-area modes in the WECC have been well studied
A good reference paper is D. Trudnowski, “Properties of the Dominant Inter-Area Modes in the WECC Interconnect,” 2012
  Four well known modes are NS Mode A (0.25 Hz), NS Mode B (or Alberta Mode), (0.4 Hz), BC Mode (0.6 Hz), Montana Mode (0.8 Hz)
Below figure from paper shows NS Mode A
On May 29, 2012

## Slide 31: Example WECC Results
Figure shows bus frequencies at several WECC buses following a large system disturbance

## Slide 32: Example WECC Results
The VPM was run simultaneously on all the signals
  Frequencies of 0.20 Hz (16% damping and 0.34 Hz (11.8% damping)
Angle of 58.7 at 0.34 Hz and 132  at 0.20 Hz
Angle of -137.1 at 0.34 Hz and 142 at 0.20 Hz

## Slide 33: Fast Fourier Transform (FFT) Applications: Motivational Example
The below graph shows a slight frequency oscillation in a transient stability run
  The question is to figure out the source of the oscillation (shown here in the bus frequency)
  Plotting all the frequency values is one option, but sometimes small oscillations could get lost
  A solution is to do an FFT