## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 12: August 14, 2003 Blackout
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 7 from the book (the term reliability is now used instead of security)
Homework 3 should be done before the exam put does not need to be turned in
First exam is Tuesday October 8 in class; closed book, closed notes. One 8.5 by 11 inch note sheet and calculators allowed
  The exam from 2018 has been posted
  Exam covers up to the end of Lecture 11

## Slide 3: On Board Sparse Vector Example

## Slide 4: Blackouts
Blackouts are costly, with some estimates of costs above $100 billion per year.
But blackouts are not created equal. Some are unavoidable due to large scale system damage (hurricanes, tornados and ice storms). Most are local, distribution issues.

## Slide 5: Some Electric Grid Risks
Image Source: Enhancing the Resilience of the Nation’s Electricity System, US National Academies Press, 2017

## Slide 6: The Real Cause of Most Blackouts!
Photo source: http://save-the-squirrels.com
But mostly only the small ones in the distribution system

## Slide 7: High-Impact, Low-Frequency Events
In order to enhance electric grid resiliency we need to consider the almost unthinkable events
These include what the North American Electric Reliability Corporation (NERC) calls High-Impact, Low-Frequency Events (HILFs); others call them black sky days
  Large-scale, potentially long duration blackouts
  HILFs identified by NERC were 1) a coordinated cyber, physical or blended attacks, 2) pandemics, 3) geomagnetic disturbances (GMDs), and 4) HEMPs
Image Source: NERC, 2012

## Slide 8: Avoidable Transmission Level Blackouts
Many major blackouts can be prevented.
Time frames of the blackouts, minutes to hours, allow for human intervention
  Tokyo 1987 (20 minutes), WECC 1996 (six minutes), Eastern Interconnect 2003 (about an hour), Italy 2003 (25 minutes)
And of course many are prevented, and hence do not make the news. For example, near voltage collapse in Delmarva Peninsula, 1999.

## Slide 9: Going Back in Time
The August 14th 2003 blackout is rapidly moving from being a “recent event” into history; yet it still has much to teach us.
This talk is about the past and the future: what can we learn from the past to help us prepare for the future
  But not so much about what are the immediate lessons from the Blackout since many recommendations have already been put into practice.
The blackout final report is very readable and available by googling “August 14 2003 Blackout Report”

## Slide 10
In contrasting numbers, the August 14 2003 Blackout hit about 50 million people, while Hurricane
Irene (2011) caused power outages affecting perhaps seven or eight million.

## Slide 11: August 14, 2003 Hoax Image
This image was widely circulated immediately after the blackout, even appearing for a time on a DOE website. It was quickly shown to be a hoax. What might immediately give it away?

## Slide 12: Actual Before and After Images

## Slide 13: Causes of the Blackout
Blackout Final Report listed four causes
  FirstEnergy (FE) did not understand inadequacies of their system, particularly with respect to voltage instability.
  Inadequate situational awareness by FE
  FE failed to adequately manage their tree growth
  Failure of the grid reliability organizations (primarily MISO) to provide effective diagnostic support
Human/cyber interactions played a key role

## Slide 14: We’ve Come Quite a Ways Since 2003
Report included 46 recommendations, many of which have dramatically changed the operation of the interconnected power grid
  Thirteen were focused on physical and cyber security
Focus of talk is what can 8/14/03 teach us to help with the grid in 2013
Need to keep in mind economic impact of 8/14/03 was above $5 billion; yearly impact of blackouts could be above $100 billion

## Slide 15: First Energy Control Center, Recent (late 2000’s)
Photo source: http://blog.cleveland.com/business/2008/12/firstenergy_corp_rejects_puco.html

## Slide 16: My Involvement in Blackout Investigation
I spend a lot of time talking to reporters on 8/14 to 8/16, before I knew what happened
Tasked by DOE to do onsite visit to FE on 8/19 to 8/21 with Doug Wiegmann; did similar visit to MISO the next week.
Did return visit in Oct
Many folks played far larger roles; I was only involved extensively early on

## Slide 17: Footprints of Reliability Coordinators in Midwest

## Slide 18: August 13, 2003
It is important to realize that immediately before the blackout few people thought the system was on the verge of a catastrophe.
NERC 2003 Summer Assessment did not list Ohio as an area of particular concern
NERC 2003 Summer Assessement is available at http://www.nerc.com/files/summer2003.pdf

## Slide 19: August 14, 2003: Pre-blackout (before 14:30 EDT)
It had mostly been a normal summer day at First Energy
  Most generation was available though the 883 MW Davis-Besse Nuclear unit was on a long-term outage
  At 13:31 EDT the Eastlake 5 unit (a 597 MW plant on Lake Erie) tripped when the operator tried to up is reactive output, but this was not seen as a severe event
It had been a busy day at MISO, with their reliability coordinators dealing with a relatively small outage in Indiana around noon
  Their state estimator failed at 1215 EDT but no one know this

## Slide 20: Cinergy Bedford-Columbus 345 kV Line Tree Contact at 12:08 EDT

## Slide 21: Trees were Finally “Trimmed” Two Months Later

## Slide 22: At 14:27 EDT Star-South Canton 345 kV Line Trips and Recloses
Star-South Canton is a tie between AEP & FE
FE missed seeing this event since their alarms had hung several minutes earlier (14:14)
    Line was back in service so it appeared normal in SCADA
    FE IT folks knew about computer problems
AEP called FE at 14:32 to check on event; FE says they saw nothing. A repeat call by AEP to FE at 15:19 also discusses event indicating ground current was detected.

## Slide 23: Estimated High Level Voltage Profile at 15:00 EDT

## Slide 24: Estimated Flows in Northeast Ohio at 15:00 EDT on August 14th 2003
Chamberlin-
Harding
345 kV Line
trips at 15:05,
an event
that was
missed by
both FE and
MISO

## Slide 25: Chamberlin-Harding was NOT on the ECAR Map (but was on FE’s Maps)
Transmission maps are available at www.eia.gov/state/maps.php

## Slide 26: Estimated Flows in Northeast Ohio at 15:06 EDT

## Slide 27: Line Outage Distribution Factors (LODFs)
LODFs are used to approximate the change in the flow on one line caused by the outage of a second line
  typically they are only used to determine the change in the MW flow
  LODFs are used extensively in real-time operations
  LODFs are state-independent (calculated using dc power flow approximations) but do dependent on the assumed network topology
  Below value tells change of real power flow on line  for the assumed outage of line k; ƒk0 is (obviously) pre-contingent

## Slide 28: Flowgates
The real-time loading of the power grid is accessed via “flowgates”
A flowgate “flow” is the real power flow on one or more transmission element for either base case conditions or a single contingency
  contingent flows are determined using LODFs
Flowgates are used as proxies for other types of limits, such as voltage or stability limits
Flowgates are calculated using a spreadsheet

## Slide 29: Flowgate #2265
Flowgate 2265 monitors the flow on FE’s Star-Juniper 345 kV line for contingent loss of the Hanna-Juniper 345 Line
  normally the LODF for this flowgate is 0.361
  flowgate has a limit of 1080 MW
  at 15:05 EDT the flow as 517 MW on Star-Juniper, 1004 MW on Hanna-Juniper, giving a flowgate value of 520+0.361*1007=884 (82%)
  Chamberlin-Harding 345 opened at 15:05; FE and MISO all missed seeing this

## Slide 30: The Bad LODF that Maybe Blacked Out the Northeast
At 15:06 EDT (after loss of Chamberlin-Harding 345) #2265 has an incorrect value because its LODF was not automatically updated.
  Value should be 633+0.463*1174=1176 (109%)
  Value was 633 + 0.361*1174=1057 (98%)
At 15:32 the flowgate’s contingent line opened, causing the flowgate to again show the correct value, about 107%

## Slide 31: Flows at 15:33 EDT

## Slide 32: Estimated Northeast Ohio 138 kV Voltage Contour: 15:33 EDT

## Slide 33: IT Issues
MISO RCs had gotten many hundreds of “alarms”
Contingency analysis results were giving pages of violations.
SE would fail because of severe system stress
Inadequate procedures for dealing with SE failure.
FE control center would get “many phone calls;” information was not effectively shared.

## Slide 34: Estimated Flows in Northeast Ohio at 15:46 EDT on August 14th 2003

## Slide 35: Estimated Northeast Ohio 138 kV Voltage Contour: 15:46 EDT

## Slide 36: What Could Have Been Done? Sammis-Star Flow Sensitivities
DOE/NERC
report said
about
1500 MW
of load
shed would have been
needed

## Slide 37: Estimated Flows in Northeast Ohio at 16:05 EDT on August 14th 2003

## Slide 38: Estimated Northeast Ohio 138 kV Voltage Contour: 16:05 EDT

## Slide 39: Path to Cleveland Blocked after Loss of Sammis-Star 16:05:57
Remaining
Paths
Image Source: August 14 2003 Blackout Final Report

## Slide 40: 345 kV Lines Trip Across Ohio to West at 16:09
ONTARIO

## Slide 41: Generation Trips 16:09:08 – 16:10:27
ONTARIO
Image Source: August 14 2003 Blackout Final Report

## Slide 42: Parts of Ohio/Michigan Served Only from Ontario after 16:10:37
Image Source: August 14 2003 Blackout Final Report

## Slide 43: Major Power Reversal: 16:10:38
Image Source: August 14 2003 Blackout Final Report

## Slide 44: Ontario/Michigan Interface Flows and Voltage
Image Source: August 14 2003 Blackout Final Report

## Slide 45: Ties from PJM to New York Open: 16:10:44 (North Ohio Black)
Image Source: August 14 2003 Blackout Final Report

## Slide 46: System Islands Break Up and Collapse: 16:10-16:13
Areas Affected by the Blackout
Service maintained
in some area
Some Local Load Interrupted
Image Source: August 14 2003 Blackout Final Report

## Slide 47: Are DC LODFs Accurate? August 14th Crash Test
Here are some results from August 14th
Time | Contingency | Element | LODF | DMW (pred) | DMW (act)
15:05 | Chamberlin-Harding 345 | Hanna-Juniper 345 | 0.362 | 179 | 176
15:32 | Hanna-Juniper 345 | Star-Juniper 345 | 0.465 | 545 | 527
15:46 | CantonCentral-Cloverdale 138 | Sammis-Star 345 | 0.164 | 48 | 54
15:46 | same | Cloverdale-Star 138 | 0.234 | 68 | 64
16:06 | Sammis-Star 345 Star-Urban 138 W.Canton-Dale 138 | Star-Juniper 345 | numerous | 517 | 676
16:06 | same | Ashtabula-Perry 345 | numerous | 319 | 408

## Slide 48: The Results are Actually Quite Good!
The initial LODF values were accurate to within a few percent
Even after more than a dozen contingencies, with many voltages well below 0.9 pu, the purely DC LODF analysis was giving fairly good (with 25%) results

## Slide 49: What Could Have Occurred on August 14th?
With 20/20 Hindsight the blackout probably could have been prevented. A smarter grid might have provided the necessary situational awareness, and/or provided the dynamic load reduction necessary to keep the system from cascading.
But key issues are 1) which grid improvement costs are cost justified, and 2) what are we missing?

## Slide 50: How Could a Smart Grid Help?
Under frequency and under voltage relays can provide quick reduction in the load, but they need to be smart enough to make the right decision
Dynamic pricing (LMPs) can help customers make economic decisions, but they depend upon a variety of “advanced applications” in order to calculate the LMPs: state estimation converging to provide the model for the SCOPF

## Slide 51: Some Thoughts on Current Needs
The data used in the models for interconnect wide studies still have significant problems
In US we have 100 GW of wind resources, but do not always have adequate models for transient stability studies; there are also potential low voltage ride through issues with solar
Power grid is rapidly changing which can result in some operational “surprises”
High impact, low frequency events are also a concern
We need people with a deep knowledge of power systems and (fill in the blank)!