## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 13: August 14, 2003 Blackout, ATC, Sensitivity Methods
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 7 from the book (the term reliability is now used instead of security)
Exam average is 83 with a high of 93.

## Slide 3: Estimated Flows in Northeast Ohio at 15:06 EDT

## Slide 4: Line Outage Distribution Factors (LODFs)
LODFs are used to approximate the change in the flow on one line caused by the outage of a second line
  typically they are only used to determine the change in the MW flow
  LODFs are used extensively in real-time operations
  LODFs are state-independent (calculated using dc power flow approximations) but do dependent on the assumed network topology
  Below value tells change of real power flow on line  for the assumed outage of line k; ƒk0 is (obviously) pre-contingent

## Slide 5: Flowgates
The real-time loading of the power grid is accessed via “flowgates”
A flowgate “flow” is the real power flow on one or more transmission element for either base case conditions or a single contingency
  contingent flows are determined using LODFs
Flowgates are used as proxies for other types of limits, such as voltage or stability limits
Flowgates are calculated using a spreadsheet

## Slide 6: Flowgate #2265
Flowgate 2265 monitors the flow on FE’s Star-Juniper 345 kV line for contingent loss of the Hanna-Juniper 345 Line
  normally the LODF for this flowgate is 0.361
  flowgate has a limit of 1080 MW
  at 15:05 EDT the flow as 517 MW on Star-Juniper, 1004 MW on Hanna-Juniper, giving a flowgate value of 520+0.361*1007=884 (82%)
  Chamberlin-Harding 345 opened at 15:05; FE and MISO all missed seeing this

## Slide 7: The Bad LODF that Maybe Blacked Out the Northeast
At 15:06 EDT (after loss of Chamberlin-Harding 345) #2265 has an incorrect value because its LODF was not automatically updated.
  Value should be 633+0.463*1174=1176 (109%)
  Value was 633 + 0.361*1174=1057 (98%)
At 15:32 the flowgate’s contingent line opened, causing the flowgate to again show the correct value, about 107%

## Slide 8: Flows at 15:33 EDT

## Slide 9: Estimated Northeast Ohio 138 kV Voltage Contour: 15:33 EDT

## Slide 10: IT Issues
MISO RCs had gotten many hundreds of “alarms”
Contingency analysis results were giving pages of violations.
SE would fail because of severe system stress
Inadequate procedures for dealing with SE failure.
FE control center would get “many phone calls;” information was not effectively shared.

## Slide 11: Estimated Flows in Northeast Ohio at 15:46 EDT on August 14th 2003

## Slide 12: Estimated Northeast Ohio 138 kV Voltage Contour: 15:46 EDT

## Slide 13: What Could Have Been Done? Sammis-Star Flow Sensitivities
DOE/NERC
report said
about
1500 MW
of load
shed would have been
needed

## Slide 14: Estimated Flows in Northeast Ohio at 16:05 EDT on August 14th 2003

## Slide 15: Estimated Northeast Ohio 138 kV Voltage Contour: 16:05 EDT

## Slide 16: Path to Cleveland Blocked after Loss of Sammis-Star 16:05:57
Remaining
Paths
Image Source: August 14 2003 Blackout Final Report

## Slide 17: 345 kV Lines Trip Across Ohio to West at 16:09
ONTARIO

## Slide 18: Generation Trips 16:09:08 – 16:10:27
ONTARIO
Image Source: August 14 2003 Blackout Final Report

## Slide 19: Parts of Ohio/Michigan Served Only from Ontario after 16:10:37
Image Source: August 14 2003 Blackout Final Report

## Slide 20: Major Power Reversal: 16:10:38
Image Source: August 14 2003 Blackout Final Report

## Slide 21: Ontario/Michigan Interface Flows and Voltage
Image Source: August 14 2003 Blackout Final Report

## Slide 22: Ties from PJM to New York Open: 16:10:44 (North Ohio Black)
Image Source: August 14 2003 Blackout Final Report

## Slide 23: System Islands Break Up and Collapse: 16:10-16:13
Areas Affected by the Blackout
Service maintained
in some area
Some Local Load Interrupted
Image Source: August 14 2003 Blackout Final Report

## Slide 24: Are DC LODFs Accurate? August 14th Crash Test
Here are some results from August 14th
Time | Contingency | Element | LODF | DMW (pred) | DMW (act)
15:05 | Chamberlin-Harding 345 | Hanna-Juniper 345 | 0.362 | 179 | 176
15:32 | Hanna-Juniper 345 | Star-Juniper 345 | 0.465 | 545 | 527
15:46 | CantonCentral-Cloverdale 138 | Sammis-Star 345 | 0.164 | 48 | 54
15:46 | same | Cloverdale-Star 138 | 0.234 | 68 | 64
16:06 | Sammis-Star 345 Star-Urban 138 W.Canton-Dale 138 | Star-Juniper 345 | numerous | 517 | 676
16:06 | same | Ashtabula-Perry 345 | numerous | 319 | 408

## Slide 25: The Results are Actually Quite Good!
The initial LODF values were accurate to within a few percent
Even after more than a dozen contingencies, with many voltages well below 0.9 pu, the purely DC LODF analysis was giving fairly good (with 25%) results

## Slide 26: What Could Have Occurred on August 14th?
With 20/20 Hindsight the blackout probably could have been prevented. A smarter grid might have provided the necessary situational awareness, and/or provided the dynamic load reduction necessary to keep the system from cascading.
But key issues are 1) which grid improvement costs are cost justified, and 2) what are we missing?

## Slide 27: How Could a Smart Grid Help?
Under frequency and under voltage relays can provide quick reduction in the load, but they need to be smart enough to make the right decision
Dynamic pricing (LMPs) can help customers make economic decisions, but they depend upon a variety of “advanced applications” in order to calculate the LMPs: state estimation converging to provide the model for the SCOPF

## Slide 28: Some Thoughts on Current Needs
The data used in the models for interconnect wide studies still have significant problems
In US we have 100 GW of wind resources, but do not always have adequate models for transient stability studies; there are also potential low voltage ride through issues with solar
Power grid is rapidly changing which can result in some operational “surprises”
High impact, low frequency events are also a concern
We need people with a deep knowledge of power systems and (fill in the blank)!

## Slide 29: General Sensitivity Analysis: Notation
We consider a system with n buses and L lines given by the set given by the set
  Some authors designate the slack as bus zero; an alternative approach, that is easier to implement in cases with multiple islands and hence slacks, is to allow any bus to be the slack, and just set its associated equations to trivial equations just stating that the slack bus voltage is constant
We may denote the kth transmission line or transformer in the system, k , as
from node
to node
28

## Slide 30: Notation, cont.
We’ll denote the real power flowing on k from bus i to bus j as ƒk
The vector of real power flows on the L lines is: which we simplify to
The bus real and reactive power injection vectors are
29

## Slide 31: Notation, cont.
The series admittance of line  is g +jb and we define
We define the LN incidence matrix
The component j of ai is nonzero whenever line i is coincident with node j. Hence A is quite sparse, with two nonzeros per row
30

## Slide 32: Analysis Example: Available Transfer Capability
The power system available transfer capability or ATC is defined as the maximum additional MW that can be transferred between two specific areas, while meeting all the specified pre- and post-contingency system conditions
ATC impacts measurably the market outcomes and system reliability and, therefore, the ATC values impact the system and market behavior
A useful reference on ATC is Available Transfer Capability Definitions and Determination from NERC, June 1996 (available online)
31

## Slide 33: ATC and Its Key Components
Total transfer capability (TTC )
  Amount of real power that can be transmitted across an interconnected transmission network in a reliable manner, including considering contingencies
Transmission reliability margin (TRM)
  Amount of TTC needed to deal with uncertainties in system conditions; typically expressed as a percent of TTC
Capacity benefit margin (CBM)
  Amount of TTC needed by load serving entities to ensure access to generation; typically expressed as a percent of TTC
32

## Slide 34: ATC and Its Key Components
Uncommitted transfer capability (UTC)
UTC  TTC – existing transmission commitment
Formal definition of ATC is
ATC  UTC – CBM – TRM
We focus on determining Um,n, the UTC from node m to node n
Um,n is defined as the maximum additional MW that can be transferred from node m to node n without violating any limit in either the base case or in any post-contingency conditions
33

## Slide 35: UTC (or TTC) Evaluation
for the base case j = 0 and each contingency case
j = 1,2 … , J
34
Goal is to load the lines up to a limit is hit

## Slide 36: Conceptual Solution Algorithm
Solve the initial power flow, corresponding to the initial system dispatch (i.e., existing commitments); set the change in transfer t(0) = 0, k=0; set step size d; j is used to indicate either the base case (j=0) or a contingency, j= 1,2,3…J
Compute t(k+1) = t(k) + d
Solve the power flow for the new t(k+1)
Check for limit violations: if violation is found set Ujm,n = t(k) and stop; else set k=k+1, and goto 2
35

## Slide 37: Conceptual Solution Algorithm, cont.
This algorithm is applied for the base case (j=0) and each specified contingency case, j=1,2,..J
The final UTC, Um,n is then determined by
This algorithm can be easily performed on parallel processors since each contingency evaluation is independent of the other
36

## Slide 38: Five Bus Example: Reference
PowerWorld Case: B5_DistFact
37

## Slide 39: Five Bus Example: Reference
 |  |  |  |  | ( MW )
 | 1 | 2 | 0 | 6.25 | 150
 | 1 | 3 | 0 | 12.5 | 400
 | 1 | 4 | 0 | 12.5 | 150
 | 2 | 3 | 0 | 12.5 | 150
 | 3 | 4 | 0 | 12.5 | 150
 | 4 | 5 | 0 | 10 | 1,000
38

## Slide 40: Five Bus Example
We evaluate U2,3 using the previous procedure
  Gradually increase generation at Bus 2 and load at Bus 3
We consider the base case and the single contingency with line 2 outaged (between 1 and 3): J = 1
Simulation results show for the base case that
And for the contingency that
Hence
39

## Slide 41: Five Bus: Maximum Base Case Transfer
40

## Slide 42: Five Bus: Maximum Contingency Transfer
41

## Slide 43: Computational Considerations
Obviously such a brute force approach can run into computational issues with large systems
Consider the following situation:
  10 iterations for each case
  6,000 contingencies
  2 seconds to solve each power flow
It will take over 33 hours to compute a single UTC for the specified transfer direction from m to n.
Consequently, there is an acute need to develop fast tools that can provide satisfactory estimates
42