## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 17: Sensitivity Methods
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 7 from the book (the term reliability is now used instead of security)
Homework 4 is due on Thursday October 31.

## Slide 3: Sensitivity Problem Formulation
Denote the system state by
Denote the conditions corresponding to the existing commitment/dispatch by s(0), p(0) and f(0) so that
the power flow equations
line real power flow vector
2

## Slide 4: Sensitivity Problem Formulation
3
g includes the real and reactive power balance equations

## Slide 5: Sensitivity Problem Formulation
For a small change, p, that moves the injection from p(0) to p(0) + p , we have a corresponding change in the state x with
We then apply a first order Taylor’s series expansion
4

## Slide 6: Sensitivity Problem Formulation
We consider this to be a “small signal” change, so we can neglect the higher order terms (h.o.t.) in the expansion
Hence we should still be satisfying the power balance equations with this perturbation; so
5

## Slide 7: Sensitivity Problem Formulation
Also, from the power flow equations, we obtain
and then just the power flow Jacobian
6

## Slide 8: Sensitivity Problem Formulation
With the standard assumption that the power flow Jacobian is nonsingular, then
We can then compute the change in the line real power flow vector
7

## Slide 9: Sensitivity Comments
Sensitivities can easily be calculated even for large systems
  If p is sparse (just a few injections) then we can use a fast forward; if sensitivities on a subset of lines are desired we could also use a fast backward
Sensitivities are dependent upon the operating point
  They also include the impact of marginal losses
Sensitivities could easily be expanded to include additional variables in x (such as phase shifter angle), or additional equations, such as reactive power flow
8

## Slide 10: Sensitivity Comments, cont.
Sensitivities are used in the optimal power flow; in that context a common application is to determine the sensitivities of an overloaded line to injections at all the buses
In the below equation, how could we quickly get these values?
  A useful reference is O. Alsac, J. Bright, M. Prais, B. Stott, “Further Developments in LP-Based Optimal Power Flow,” IEEE. Trans. on Power Systems, August 1990, pp. 697-711; especially see equation 3.
9

## Slide 11: Sensitivity Example in PowerWorld
Open case B5_DistFact and then Select Tools, Sensitivities, Flow and Voltage Sensitivities
  Select Single Meter, Multiple Transfers, Buses page
  Select the Device Type (Line/XFMR), Flow Type (MW), then select the line (from Bus 2 to Bus 3)
  Click Calculate Sensitivities; this shows impact of a single injection going to the slack bus (Bus 1)
  For our example of a transfer from 2 to 3 the value is the result we get for bus 2 (0.5440) minus the result for bus 3 (-0.1808) = 0.7248
  With a flow of 118 MW, we would hit the 150 MW limit with (150-118)/0.7248 =44.1MW, close to the limit we found of 45MW
10

## Slide 12: Sensitivity Example in PowerWorld
If we change the conditions to the anticipated maximum loading (changing the load at 2 from 118 to 118+44=162 MW) and we re-evaluate the sensitivity we note it has changed little (from -0.7248 to -0.7241)
  Hence a linear approximation (at least for this scenario) could be justified
With what we know so far, to handle the contingency situation, we would have to simulate the contingency, and reevaluate the sensitivity values
  We’ll be developing a quicker (but more approximate) approach next
11

## Slide 13: Linearized Sensitivity Analysis
By using the approximations from the fast decoupled power flow we can get sensitivity values that are independent of the current state. That is, by using the B’ and B’’ matrices
For line flow we can approximate
12

## Slide 14: Linearized Sensitivity Analysis
Also, for each line 
and so,

## Slide 15: Sensitivity Analysis: Recall the Matrix Notation
The series admittance of line  is g +jb and we define
We define the LN incidence matrix
where the component j of ai is nonzero whenever line i is coincident with node j. Hence A is quite sparse, with at most two nonzeros per row

## Slide 16: Linearized Active Power Flow Model
Under these assumptions the change in the real power line flows are given as
The constant matrix is called the injection shift factor matrix (ISF)
15

## Slide 17: Injection Shift Factors (ISFs)
The element in row  and column n of  is called the injection shift factor (ISF) of line  with respect to the injection at node n
  Absorbed at the slack bus, so it is slack bus dependent
Terms generation shift factor (GSF) and load shift factor (LSF) are also used (such as by NERC)
  Same concept, just a variation in the sign whether it is a generator or a load
  Sometimes the associated element is not a single line, but rather a combination of lines (an interface)
Terms used in North America are defined in the NERC glossary (http://www.nerc.com/files/glossary_of_terms.pdf)
16

## Slide 18: ISF Interpretation
is the fraction of the additional 1 MW injection at node n that goes though line 
slack
node
17

## Slide 19: ISF Properties
By definition, depends on the location of the slack bus
By definition, for since the injection and withdrawal buses are identical in this case and, consequently, no flow arises on any line 
The magnitude of is at most 1 since
Note, this is strictly true only for the linear (lossless) case. In the nonlinear case, it is possible that a transaction decreases losses. Hence a 1 MW injection could change a line flow by more than 1 MW.
18

## Slide 20: Five Bus Example Reference
19

## Slide 21: Five Bus ISF, Line 4, Bus 2 (to Slack)
20

## Slide 22: Five Bus Example
The row of A correspond to
the lines and transformers,
the columns correspond to
the non-slack buses (buses 2
to 5); for each line there
is a 1 at one end, a -1 at the
other end (hence an
assumed sign convention!).
Here we put a 1 for the
lower numbered bus, so positive flow is assumed from the lower numbered bus to the higher number
21

## Slide 23: Five Bus Example
22
With bus 1 as the slack, the buses (columns) go for 2 to 5

## Slide 24: Five Bus Example Comments
At first glance the numerically determined value of (128-118)/20=0.5 does not match closely with the analytic value of 0.5455; however, in doing the subtraction we are losing numeric accuracy
  Adding more digits helps (128.40 – 117.55)/20 = 0.5425
The previous matrix derivation isn’t intended for actual computation;  is a full matrix so we would seldom compute all of its values
Sparse vector methods can be used if we are only interested in the ISFs for certain lines and certain buses
23

## Slide 25: Distribution Factors
Various additional distribution factors may be defined
  power transfer distribution factor (PTDF)
  line outage distribution factor (LODF)
  line addition distribution factor (LADF)
  outage transfer distribution factor (OTDF)
These factors may be derived from the ISFs making judicious use of the superposition principle
24

## Slide 26: Definition: Basic Transaction
A basic transaction involves the transfer of a specified amount of power t from an injection node m to a withdrawal node n
25

## Slide 27: Definition: Basic Transaction
We use the notation
to denote a basic transaction
injection node
withdrawal node
quantity
26

## Slide 28: Definition: PTDF
NERC defines a PTDF as
  “In the pre-contingency configuration of a system under study, a measure of the responsiveness or change in electrical loadings on transmission system Facilities due to a change in electric power transfer from one area to another, expressed in percent (up to 100%) of the change in power transfer”
  Transaction dependent
We’ll use the notation to indicate the PTDF on line  with respect to basic transaction w
In the lossless formulation presented here (and commonly used) it is slack bus independent
27

## Slide 29: PTDFs
Note, the PTDF is independent of the amount t; which is often expressed as a percent
28

## Slide 30: PTDF Evaluation in Two Parts
=
+
29

## Slide 31: PTDF Evaluation
30

## Slide 32: Calculating PTDFs in PowerWorld
PowerWorld provides a number of options for calculating and visualizing PTDFs
  Select Tools, Sensitivities, Power Transfer Distribution Factors (PTDFs)
Results are shown for the five bus case for the Bus 2 to Bus 3 transaction
31

## Slide 33: Five Bus PTDF Visualization
PowerWorld Case: B5_DistFact_PTDF
32

## Slide 34: Nine Bus PTDF Example
PowerWorld Case: B9_PTDF
Display shows the PTDFs for a basic transaction from Bus A to Bus I. Note that 100% of the transaction leaves Bus A and 100% arrives at Bus I
33

## Slide 35: Eastern Interconnect Example: Wisconsin Utility to TVA PTDFs
In this example multiple generators contribute for both the seller and the buyer
Contours show lines that would carry at least 2% of a power transfer from Wisconsin to TVA
34

## Slide 36: Line Outage Distribution Factors (LODFs)
Power system operation is practically always limited by contingencies, with line outages comprising a large number of the contingencies
Desire is to determine the impact of a line outage (either a transmission line or a transformer) on other system real power flows without having to explicitly solve the power flow for the contingency
These values are provided by the LODFs
The LODF is the portion of the pre-outage real power line flow on line k that is redistributed to line  as a result of the outage of line k
35

## Slide 37: LODFs
outaged
base case
outage case
Best reference is Chapter 7 of the course book
36

## Slide 38: LODF Evaluation
We simulate the impact of the outage of line k by adding the basic transaction
and selecting tk in such a way that the flows on the dashed lines become exactly zero
In general this tk is not equal to the original line flow
37

## Slide 39: LODF Evaluation
We select tk to be such that
where ƒ k is the active power flow change on the line k due to the transaction wk
The line k flow from wk depends on its PTDF
it follows that
38

## Slide 40: LODF Evaluation
For the rest of the network, the impacts of the outage of line k are the same as the impacts of the additional basic transaction wk
Therefore, by definition the LODF is
39

## Slide 41: Five Bus Example
Assume we wish to calculate the values for the outage of line 4 (between buses 2 and 3); this is line k
Say we wish to know the change in flow on the line 3 (Buses 3 to 4). PTDFs for a transaction from 2 to 3 are 0.7273 on line 4 and 0.0909 on line 3
40

## Slide 42: Five Bus Example
Hence we get
41

## Slide 43: Five Bus Example Compensated
Here is the system with the compensation added to bus 2 and removed at bus 3; we are canceling the impact of the line 4 flow for the reset of the network.
42

## Slide 44: Five Bus Example
Below we see the network with the line actually outaged
The line 3 flow changed from 63 MW to 106 MW, an increase of 43 MW, matching the LODF value
43