## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 16: Sensitivity Methods, Least Squares
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 9 from the book
Homework 4 is due on Thursday October 31.

## Slide 3: Line Outage Distribution Factors (LODFs)
Power system operation is practically always limited by contingencies, with line outages comprising a large number of the contingencies
Desire is to determine the impact of a line outage (either a transmission line or a transformer) on other system real power flows without having to explicitly solve the power flow for the contingency
These values are provided by the LODFs
The LODF is the portion of the pre-outage real power line flow on line k that is redistributed to line  as a result of the outage of line k
2

## Slide 4: LODFs
outaged
base case
outage case
Best reference is Chapter 7 of the course book
3

## Slide 5: LODF Evaluation
We simulate the impact of the outage of line k by adding the basic transaction
and selecting tk in such a way that the flows on the dashed lines become exactly zero
In general this tk is not equal to the original line flow
4

## Slide 6: LODF Evaluation
We select tk to be such that
where ƒ k is the active power flow change on the line k due to the transaction wk
The line k flow from wk depends on its PTDF
it follows that
5

## Slide 7: LODF Evaluation
For the rest of the network, the impacts of the outage of line k are the same as the impacts of the additional basic transaction wk
Therefore, by definition the LODF is
6

## Slide 8: Five Bus Example
Assume we wish to calculate the values for the outage of line 4 (between buses 2 and 3); this is line k
Say we wish to know the change in flow on the line 3 (Buses 3 to 4). PTDFs for a transaction from 2 to 3 are 0.7273 on line 4 and 0.0909 on line 3
7

## Slide 9: Five Bus Example
Hence we get
8

## Slide 10: Five Bus Example Compensated
Here is the system with the compensation added to bus 2 and removed at bus 3; we are canceling the impact of the line 4 flow for the reset of the network.
9

## Slide 11: Five Bus Example
Below we see the network with the line actually outaged
The line 3 flow changed from 63 MW to 106 MW, an increase of 43 MW, matching the LODF value
10

## Slide 12: Developing a Critical Eye
In looking at the below formula you need to be thinking about what conditions will cause the formula to fail Here the obvious situation is when the denominator is zero
That corresponds to a situation in which the contingency causes system islanding
  An example is line 6 (between buses 4 and 5)
  Impact modeled by injections at the buses within each viable island
11

## Slide 13: Calculating LODFs in PowerWorld
Select Tools, Sensitivities, Line Outage Distribution Factors
  Select the Line using dialogs on right, and click Calculate LODFS; below example shows values for line 4
12

## Slide 14: Blackout Case LODFs
One of the issues associated with the 8/14/03 blackout was the LODF associated with the loss of the Hanna-Juniper 345 kV line (21350-22163) that was being used in a flow gate calculation was not correct because the Chamberlin-Harding 345 kV line outage was missed
  With the Chamberlin-Harding line assumed in-service the value was 0.362
  With this line assumed out-of-service (which indeed it was) the value increased to 0.464
13

## Slide 15: 2000 Bus LODF Example
LODF is for line between 3048 and 5120; values will be proportional to the PTDF values
14

## Slide 16: 2000 Bus LODF Example
15
Image visualizes the PTDFs between buses 3048 and 5120

## Slide 17: Multiple Line LODFs
LODFs can also be used to represent multiple device contingencies, but it is usually more involved than just adding the effects of the single device LODFs
Assume a simultaneous outage of lines k1 and k2
Now setup two transactions, wk1 (with value tk1)and wk2 (with value tk2) so
16

## Slide 18: Multiple Line LODFs
Hence we can calculate the simultaneous impact of multiple outages; details for the derivation are given in C.Davis, T.J. Overbye, "Linear Analysis of Multiple Outage Interaction," Proc. 42nd HICSS, 2009
Equation for the change in flow on line  for the outage of lines k1 and k2 is
17

## Slide 19: Multiple Line LODFs
Example: Five bus case, outage of lines 2 and 5 to flow on line 4.
18

## Slide 20: Multiple Line LODFs
Flow goes from 117.5 to 118.0
19

## Slide 21: Line Closure Distribution Factors (LCDFs)
Closed line
base case
line k addition case
20

## Slide 22: LCDF Definition
The line closure distribution factor (LCDF), LCDF,k, for the closure of line k (or its addition if it does not already exist) is the portion of the line active power flow on line k that is distributed to line  due to the closure of line k
Since line k is currently open, the obvious question is, "what flow on line k?"
Answer (in a dc power flow sense) is the flow that will occur when the line is closed (which we do not know)
21

## Slide 23: LCDF Evaluation
We simulate the impact of the closure of line k by imposing the additional basic transaction
on the base case network and we select tk so that
22

## Slide 24: LCDF Evaluation
For the other parts of the network, the impacts of the addition of line k are the same as the impacts of adding the basic transaction wk
Therefore, the definition is
The post-closure flow ƒk is determined (in a dc power flow sense) as the flow that would occur from the angle difference divided by (1 + )
23

## Slide 25: Outage Transfer Distribution Factor
The outage transfer distribution factor (OTDF) is defined as the PTDF with the line k outaged
The OTDF applies only to the post-contingency configuration of the system since its evaluation explicitly considers the line k outage
This is a quite important value since power system operation is usually contingency constrained
24

## Slide 26: Outage Transfer Distribution Factor (OTDF)
outaged
line
25

## Slide 27: OTDF Evaluation
=
+
26

## Slide 28: OTDF Evaluation
Since
and
then so that
27

## Slide 29: Five Bus Example
Say we would like to know the PTDF on line 1 for a transaction between buses 2 and 3 with line 2 out
28

## Slide 30: Five Bus Example
Hence we want to calculate these values without having to explicitly outage line 2
Hence the value we are looking for is 0.2 (20%)
29

## Slide 31: Five Bus Example
Evaluating: the PTDF for the bus 2 to 3 transaction on line 1 is 0.2727; it is 0.1818 on line 2 (from buses 1 to 3); the LODF is on line 1 for the outage of line 2 is -0.4
Hence
For line 4 (buses 2 to 3) the value is
30

## Slide 32: August 14, 2003 OTDF Example
Flowgate 2264 monitored the flow on Star-Juniper 345 kV line for contingent loss of Hanna-Juniper 345 kV normally the LODF for this flowgate is 0.361
  flowgate had a limit of 1080 MW
  at 15:05 EDT the flow as 517 MW on Star-Juniper, 1004 MW on Hanna-Juniper, giving a flowgate value of 520+0.361*1007=884 (82%)
  Chamberlin-Harding 345 opened at 15:05, but was missed
  At 15:06 EDT (after loss of Chamberlin-Harding 345) #2265 had an incorrect value because its LODF was not updated.
  Value should be 633+0.463*1174=1176 (109%)
  Value was 633 + 0.361*1174=1057 (98%)
31

## Slide 33: UTC Revisited
We can now revisit the uncommitted transfer capability (UTC) calculation using PTDFs and LODFs
Recall trying to determine maximum transfer between two areas (or buses in our example)
For base case maximums are quickly determined with PTDFs
Note we are ignoring zero (or small) PTDFs; would also need to consider flow reversal
32

## Slide 34: UTC Revisited
For the contingencies we use
Then as before
We would need to check all contingencies! Also, this is just a linear estimate and is not considering voltage violations.
33

## Slide 35: Five Bus Example
34

## Slide 36: Five Bus Example
Therefore, for the base case
35

## Slide 37: Five Bus Example
For the contingency case corresponding to the outage of the line 2 The limiting value is line 4
Hence the UTC is limited by the contingency to 23.0
36

## Slide 38: Additional Comments
Distribution factors are defined as small signal sensitivities, but in practice, they are also used for simulating large signal cases
Distribution factors are widely used in the operation of the electricity markets where the rapid evaluation of the impacts of each transaction on the line flows is required
Applications to actual system show that the distribution factors provide satisfactory results in terms of accuracy
For multiple applications that require fast turn around time, distribution factors are used very widely, particularly, in the market environment
They do not work well with reactive power!
37

## Slide 39: Least Squares
So far we have considered the solution of Ax = b in which A is a square matrix; as long as A is nonsingular there is a single solution
  That is, we have the same number of equations (m) as unknowns (n)
Many problems are overdetermined in which there more equations than unknowns (m > n)
  Overdetermined systems are usually inconsistent, in which no value of x exactly solves all the equations
Underdetermined systems have more unknowns than equations (m < n); they never have a unique solution but are usually consistent
38

## Slide 40: Method of Least Squares
The least squares method is a solution approach for determining an approximate solution for an overdetermined system
If the system is inconsistent, then not all of the equations can be exactly satisfied
The difference for each equation between its exact solution and the estimated solution is known as the error
Least squares seeks to minimize the sum of the squares of the errors
Weighted least squares allows differ weights for the equations
39

## Slide 41: Least Squares Solution History
The method of least squares developed from trying to estimate actual values from a number of measurements
Several persons in the 1700's, starting with Roger Cotes in 1722, presented methods for trying to decrease model errors from using multiple measurements
Legendre presented a formal description of the method in 1805; evidently Gauss claimed he did it in 1795
Method is widely used in power systems, with state estimation the best known application, dating from Fred Schweppe's work in 1970
40

## Slide 42: Least Squares and Sparsity
In many contexts least squares is applied to problems that are not sparse. For example, using a number of measurements to optimally determine a few values
  Regression analysis is a common example, in which a line or other curve is fit to potentially many points)
  Each measurement impacts each model value
In the classic power system application of state estimation the system is sparse, with measurements only directly influencing a few states
  Power system analysis classes have tended to focus on solution methods aimed at sparse systems; we'll consider both sparse and nonsparse solution methods
41

## Slide 43: Least Squares Problem
Consider
or
42

## Slide 44: Least Squares Solution
We write (ai)T for the row i of A and ai is a column vector
Here, m ≥ n and the solution we are seeking is that which minimizes Ax - bp, where p denotes some norm
Since usually an overdetermined system has no exact solution, the best we can do is determine an x that minimizes the desired norm.
43

## Slide 45: Choice of p
We discuss the choice of p in terms of a specific example
Consider the equation Ax = b with
(hence three equations and one unknown)
We consider three possible choices for p:
44

## Slide 46: Choice of p
(i) p = 1
(ii) p = 2
(iii) p = 
45