## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 17: Least Squares, State Estimation
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 9 from the book
Homework 4 is due on Thursday October 31.

## Slide 3: Least Squares Solution
We write (ai)T for the row i of A and ai is a column vector
Here, m ≥ n and the solution we are seeking is that which minimizes Ax - bp, where p denotes some norm
Since usually an overdetermined system has no exact solution, the best we can do is determine an x that minimizes the desired norm.
2

## Slide 4: Choice of p
We discuss the choice of p in terms of a specific example
Consider the equation Ax = b with
(hence three equations and one unknown)
We consider three possible choices for p:
3

## Slide 5: Choice of p
(i) p = 1
(ii) p = 2
(iii) p = 
4

## Slide 6: The Least Squares Problem
In general, is not differentiable for p = 1 or p = ∞
The choice of p = 2 (Euclidean norm) has become well established given its least-squares fit interpretation
The problem is tractable for 2 major reasons
  First, the function is differentiable
5

## Slide 7: The Least Squares Problem, cont.
  Second, the Euclidean norm is preserved under orthogonal transformations: with Q an arbitrary orthogonal matrix; that is, Q satisfies
6

## Slide 8: The Least Squares Problem, cont.
We introduce next the basic underlying assumption: A is full rank, i.e., the columns of A constitute a set of linearly independent vectors
This assumption implies that the rank of A is n because n ≤ m since we are dealing with an overdetermined system
Fact: The least squares solution x* satisfies
7

## Slide 9: Proof of Fact
Since by definition the least squares solution x* minimizes at the optimum, the derivative of this function zero:
8

## Slide 10: Implications
This underlying assumption implies that
Therefore, the fact that ATA is positive definite (p.d.) follows from considering any x ≠ 0 and evaluating
which is the definition of a p.d. matrix
We use the shorthand ATA > 0 for ATA being a symmetric, positive definite matrix
9

## Slide 11: Implications
The underlying assumption that A is full rank and therefore ATA is p.d. implies that there exists a unique least squares solution
Note: we use the inverse in a conceptual, rather than a computational, sense
The below formulation is known as the normal equations, with the solution conceptually straightforward
10

## Slide 12: Example: Curve Fitting
Say we wish to fit five points to a polynomial curve of the form
This can be written as

## Slide 13: Example: Curve Fitting
Say the points are t =[0,1,2,3,4] and y = [0,2,4,5,4]. Then

## Slide 14: Implications
An important implication of positive definiteness is that we can factor ATA since ATA > 0
The expression ATA = GTG is called the Cholesky factorization of the symmetric positive definite matrix ATA
13

## Slide 15: A Least Squares Solution Algorithm
  Step 1: Compute the lower triangular part of ATA
  Step 2: Obtain the Cholesky Factorization
  Step 3: Compute
  Step 4: Solve for y using forward substitution in
  and for x using backward substitution in
14
Note, our standard LU factorization approach would work; we can just solve it twice as fast by taking advantage of it being a symmetric matrix

## Slide 16: Practical Considerations
The two key problems that arise in practice with the triangularization procedure are:
  First, while A maybe sparse, ATA is much less sparse and consequently requires more computing resources for the solution
    In particular, with ATA second neighbors are now connected! Large networks are still sparse, just not as sparse
  Second, ATA may actually be numerically less well-conditioned than A
15

## Slide 17: Loss of Sparsity Example
Assume the B matrix for a network is
Then BTB is
Second neighbors are now connected!
16

## Slide 18: Numerical Conditioning
To understand the point on numerical ill- conditioning, we need to introduce terminology
We define the norm of a matrix to be
This is the maximum singular value of B
17

## Slide 19: Numerical Conditioning Example
Say we have the matrix
What value of x with a norm of 1 that maximizes ?
What value of x with a norm of 1 that minimizes ?
18

## Slide 20: Numerical Conditioning
i.e., li is a root of the polynomial
In other words, the 2 norm of B is the square root of the largest eigenvalue of BTB
19
Keep in mind the eigenvalues of a p.d. matrix are
positive

## Slide 21: Numerical Conditioning
The conditioning number of a matrix B is defined as
A well–conditioned matrix has a small value of
, close to 1; the larger the value of , the more pronounced is the ill-conditioning
20

## Slide 22: Power System State Estimation
Overall goal is to come up with a power flow model for the present "state" of the power system based on the actual system measurements
SE assumes the topology and parameters of the transmission network are mostly known
Measurements come from SCADA, and increasingly, from PMUs
21

## Slide 23: Power System State Estimation
Problem can be formulated in a nonlinear, weighted least squares form as where J(x) is the scalar cost function, x are the state variables (primarily bus voltage magnitudes and angles), zi are the m measurements, f(x) relates the states to the measurements and i is the assumed standard deviation for each measurement
22

## Slide 24: Assumed Error
Hence the goal is to decrease the error between the measurements and the assumed model states x
The i term weighs the various measurements, recognizing that they can have vastly different assumed errors
Measurement error is assumed Gaussian (whether it is or not is another question); outliers (bad measurements) are often removed
23

## Slide 25: State Estimation for Linear Functions
First we’ll consider the linear problem. That is where
Let R be defined as the diagonal matrix of the variances (square of the standard deviations) for each of the measurements
24

## Slide 26: State Estimation for Linear Functions
We then differentiate J(x) w.r.t. x to determine the value of x that minimizes this function
25

## Slide 27: Simple DC System Example
Say we have a two bus power system that we are solving using the dc approximation. Say the line’s per unit reactance is j0.1. Say we have power measurements at both ends of the line. For simplicity assume R=I. We would then like to estimate the bus angles. Then
We have a problem since HTH is singular. This is because of lack of an angle reference.
26

## Slide 28: Simple DC System Example, cont.
Say we directly measure q1 (with a PMU) to be zero; set this as the third measurement. Then
27
Note that the angles are in radians

## Slide 29: Nonlinear Formulation
A regular ac power system is nonlinear, so we need to use an iterative solution approach. This is similar to the Newton power flow. Here assume m measurements and n state variables (usually bus voltage magnitudes and angles) Then the Jacobian is the H matrix