## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 5: Power Flow
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
RSVP to Alex at zandra23@ece.tamu.edu for the TAMU ECE Energy and Power Group (EPG) picnic. It starts at 5pm on September 27, 2019
Read Chapter 6 from the book
  They formulate the power flow using the polar form for the Ybus elements
Homework 1 is due on Thursday September 12

## Slide 3: Three Bus Case on AGC
Net tie flow is
close to zero
Generation
is automatically
changed to match
change in load

## Slide 4: Generator Costs
There are many fixed and variable costs associated with power system operation
The major variable cost is associated with generation.
Cost to generate a MWh can vary widely
For some types of units (such as hydro and nuclear) it is difficult to quantify
More others such as wind and solar the marginal cost of energy is essentially zero (actually negative for wind!)
For thermal units it is straightforward to determine
Many markets have moved from cost-based to price-based generator costs

## Slide 5: Economic Dispatch
Economic dispatch (ED) determines the least cost dispatch of generation for an area.
For a lossless system, the ED occurs when all the generators have equal marginal costs. IC1(PG,1) = IC2(PG,2) = … = ICm(PG,m)

## Slide 6: Power Transactions
Power transactions are contracts between areas to do power transactions.
Contracts can be for any amount of time at any price for any amount of power.
Scheduled power transactions are implemented by modifying the area ACE: ACE = Pactual,tie-flow - Psched

## Slide 7: 100 MW Transaction
Scheduled 100 MW transaction from the Home Area to the Other Area
Net tie-line
flow is now
100 MW

## Slide 8: Security Constrained ED
Transmission constraints often limit system economic operation.
Such limits required a constrained dispatch in order to maintain system security.
In the three bus case the generation at bus 3 must be constrained to avoid overloading the line from bus 2 to bus 3.

## Slide 9: Security Constrained Dispatch
Dispatch is no longer optimal due to need to keep the line
from bus 2 to bus 3 from overloading

## Slide 10: Multi-Area Operation
If areas have direct interconnections then they may directly transact, up to the capacity of their tie-lines.
Actual power flows through the entire network according to the impedance of the transmission lines.
Flow through other areas is known as “parallel path” or “loop flow.”

## Slide 11: Seven Bus Case: One-line
System has three areas
Area Left
has one
bus
Area Right has one bus
Area Top
has five
buses
PowerWorld Case: B7Flat

## Slide 12: Seven Bus Case: Area View
System has
40 MW of
“Loop Flow”
Actual
flow
between
areas
Scheduled
flow

## Slide 13: Seven Bus - Loop Flow?
100 MW Transaction
between Left and Right
Transaction has actually decreased
the loop flow
Note that
Top’s
losses have
increased
from
7.1 MW to
9.6 MW

## Slide 14: Power Transfer Distribution Factors (PTDFS)
PTDFs are used to show how a particular transaction will affect the system
The power transfers through the system according to the impedances of the lines, without respect to ownership
All transmission players in network could potentially be impacted (to a greater or lesser extent)
Later in the semester we’ll consider techniques for calculating PTDFs

## Slide 15: PTDF Example: Nine Bus System, Actual Flows
PowerWorld Case: B9

## Slide 16: PTDF Example: Nine Bus System, Transfer from A to I
Values now tell percentage of flow that will go on line

## Slide 17: PTDF Example: Nine Bus System, Transfer From G to F
Values now tell percentage of flow that will go on line

## Slide 18: Wisconsin to TVA Line PTDF Contour
Contours show lines that would carry at least 2% of a power transfer from Wisconsin to TVA

## Slide 19: NERC Flowgates
A convenient glossary of terms used for power system operations in North America is available at http://www.nerc.com/files/glossary_of_terms.pdf
One common term is a “flowgate,” which is a mathematical construct to measure the MW flow on one or more elements in the bulk transmission system
  Sometimes they include the impact of contingencies, something we will consider later in the semester
A simple flowgate would be the MW flow through a single transmission line or transformer

## Slide 20: NERC TLRs
In the North American transmission loading relief procedures (TLRs) are used to mitigate the overloads on the bulk transmission system
  https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-006-5.pdf
  Called TLR in the East, WECC Unscheduled Flow Mitigation or Congestion Management Procedures (ERCOT)
In the Eastern Interconnect TLRs consider the PTDFs associated with transactions on flowgates if there is a flowgate violation

## Slide 21: Loop Flow Impact: Market Segmentation
During summer
of 1998 con-
gestion on just
two elements
pushed Midwest
spot market
prices up by a
factor of 200:
from $ 20/MWh
to $ 7500/MWh!

## Slide 22: Pricing Electricity
Cost to supply electricity to bus is called the locational marginal price (LMP)
Presently some electric markets post LMPs on the web
In an ideal electricity market with no transmission limitations the LMPs are equal
Transmission constraints can segment a market, resulting in differing LMP
Determination of LMPs requires the solution on an Optimal Power Flow (OPF), which will be covered later in the semester

## Slide 23: Three Bus LMPs – Constraints Ignored
Line from Bus 1 to Bus 3 is over-loaded; all buses have same marginal cost
Gen 1’s
cost
is $10
per
MWh
Gen 2’s
cost
is $12
per
MWh
PowerWorld Case: B3LP

## Slide 24: Three Bus LMPs – Constraint Unforced
Line from 1 to 3 is no longer overloaded, but now
the marginal cost of electricity at bus 3 is $14 / MWh

## Slide 25: MISO LMPs on 9/6/2019, 3:35 PM
Five minute LMPs are posted online for the MISO footprint
Source: https://www.misoenergy.org/markets-and-operations/real-time--market-data/real-time-displays/

## Slide 26: ERCOT LMPS: 5/5/18 and 9/6/19
Image Source: http://www.ercot.com/content/cdr/contours/rtmLmp.html

## Slide 27: Advanced Power Flow
Next slides cover some more advanced power flow topics that need to be considered in many commercial power flow studies
An important consideration in the power flow is the assumed time scale of the response, and the assumed model of operator actions
  Planning power flow studies usually assume automatic modeling of operator actions and a longer time frame of response (controls have time to reach steady-state)
    For example, who is actually doing the volt/var control
  In real-time applications operator actions are usually not automated and controls may be more limited in time

## Slide 28: Power Flow Optimal Multiplier
Classic reference on power flow optimal multiplier is S. Iwamoto, Y. Tamura, “A Load Flow Calculation Method for Ill-Conditioned Power Systems,” IEEE Trans. Power App. and Syst., April 1981
Another paper is J.E. Tate, T.J. Overbye, “A Comparison of the Optimal Multiplier in Power and Rectangular Coordinates,” IEEE Trans. Power Systems, Nov. 2005
Key idea is once NR method has selected a direction, we can analytically determine the distance to move in that direction to minimize the norm of the mismatch
  Goal is to help with stressed power systems

## Slide 29: Power Flow with Optimal Multiplier
Consider an n bus power system with f(x) = S where S is the vector of the constant real and reactive power load minus generation at all buses except the slack, x is the vector of the bus voltages in rectangular coordinates: Vi = ei + jfi, and f is the function of the power balance constraints

## Slide 30: Power Flow with Optimal Multiplier
With a standard NR approach we would get
If we are close enough to the solution the iteration converges quickly, but if the system is heavily loaded it can diverge

## Slide 31: Power Flow with Optimal Multiplier
Optimal multiplier approach modifies the iteration as
Scalar m is chosen to minimize the norm of the mismatch F in direction x
Paper by Iwamoto, Y. Tamura from 1981 shows m can be computed analytically with little additional calculation when rectangular voltages are used

## Slide 32: Power Flow with Optimal Multiplier
Determination of m involves solving a cubic equation, which gives either three real solutions, or one real and two imaginary solutions
1989 PICA paper by Iba (“A Method for Finding a Pair of Multiple Load Flow Solutions in Bulk Power Systems”) showed that NR tends to converge along line joining the high and a low voltage solution
However, there are some model restrictions

## Slide 33: Quasi-Newton Power Flow Methods
First we consider some modified versions of the Newton power flow (NPF)
Since most of the computation in the NPF is associated with building and factoring the Jacobian matrix, J, the focus is on trying to reduce this computation
In a pure NPF J is build and factored each iteration
Over the years pretty much every variation of the NPF has been tried; here we just touch on the most common
Whether a method is effective can be application dependent
  For example, in contingency analysis we are usually just resolving a solved case with an often small perturbation

## Slide 34: Quasi-Newton Power Flow Methods
The simplest modification of the NPF results when J is kept constant for a number of iterations, say k iterations
  Sometimes known as the Dishonest Newton
The approach balances increased speed per iteration, with potentially more iterations to perform
There is also an increased possibility for divergence
Since the mismatch equations are not modified, if it converges it should converge to the same solution as the NPF
These methods are not commonly used, except in very short duration, sequential power flows with small mismatches

## Slide 35: Dishonest N-R Example
We pay a price
in increased
iterations, but
with decreased
computation
per iteration; that price is too high in this example

## Slide 36: NPF (Honest) Region of for Two Bus Example Convergence
Red region
converges
to the high
voltage
solution,
while the
yellow region
converges
to the low
voltage
solution
Maximum of 15
iterations

## Slide 37: Two Bus Dishonest ROC
In this case being honest pays! At least with respect to the region of convergence
(ROC)

## Slide 38: Quasi-Newton Power Flow Methods
A second modification is to modify the step size in the direction given by the NPF
  This is one we’ve already considered with the optimal multiplier approach
The generalized approach is to solve what is known as the line search (i.e., a one-dimensional optimization) to determine 

## Slide 39: The Single Dimensional  (l)
0

## Slide 40: Line Search
We need a cost function, which is usually the Euclidean norm of the mismatch vector
The line search is a general optimization problem for which there are many potential solution approaches
  Determines a local optimum within some search boundaries
  Approaches depend on whether there is gradient information available
Aside from the optimal multiplier approach, which can be quite helpful with little additional computation, the convergence gain from determining the “optimal”  is usually more than offset by the line search computation

## Slide 41: Decoupled Power Flow
Rather than not updating the Jacobian, the decoupled power flow takes advantage of characteristics of the power grid in order to decouple the real and reactive power balance equations
  There is a strong coupling between real power and voltage angle, and reactive power and voltage magnitude
  There is a much weaker coupling between real power and voltage angle, and reactive power and voltage angle
Key reference is B. Stott, “Decoupled Newton Load Flow,” IEEE Trans. Power. App and Syst., Sept/Oct. 1972, pp. 1955-1959

## Slide 42: Decoupled Power Flow Formulation

## Slide 43: Decoupling Approximation

## Slide 44: Off-diagonal Jacobian Terms
By assuming ½ the elements are zero, we only have to do ½ the computations

## Slide 45: Decoupled N-R Region of Convergence
The high solution ROC is actually larger than with the standard NPF. Obviously this is not a good a way to get the low
solution

## Slide 46: Fast Decoupled Power Flow
By continuing with our Jacobian approximations we can actually obtain a reasonable approximation that is independent of the voltage magnitudes/angles.
This means the Jacobian need only be built/inverted once per power flow solution
This approach is known as the fast decoupled power flow (FDPF)

## Slide 47: Fast Decoupled Power Flow, cont.
FDPF uses the same mismatch equations as standard power flow (just scaled) so it should have same solution
The FDPF is widely used, though usually only when we only need an approximate solution
Key fast decoupled power flow reference is B. Stott, O. Alsac, “Fast Decoupled Load Flow,” IEEE Trans. Power App. and Syst., May 1974, pp. 859-869
Modified versions also exist, such as D. Jajicic and A. Bose, “A Modification to the Fast Decoupled Power Flow for Networks with High R/X Ratios, “IEEE Transactions on Power Sys., May 1988, pp. 743-746

## Slide 48: FDPF Approximations
To see the impact on the real power equations recall

## Slide 49: FDPF Approximations
With the approximations for the diagonal term we get
Hence the Jacobian for the real equations can be approximated as –B

## Slide 50: FPDF Approximations
For the reactive power equations we also scale by Vi
For the Jacobian off-diagonals we get

## Slide 51: FDPF Approximations
And for the reactive power Jacobian diagonal we get
As derived the real and reactive equations have a constant Jacobian equal to –B
  Usually modifications are made to omit from the real power matrix elements that affect reactive flow (like shunts) and from the reactive power matrix elements that affect real power flow, like phase shifters
  We’ll call the real power matrix B’ and the reactive B”