## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 7: Advanced Power Flow
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 6 from the book
  They formulate the power flow using the polar form for the Ybus elements
Homework 2 is due on Thursday September 26

## Slide 3: Aggieland37 With Phase Shifters
PowerWorld Case: Aggieland37_PhaseShifter

## Slide 4: Large Case Phase Shifter Limits and Step Size

## Slide 5: Impedance Correction Tables
With taps the impedance of the transformer changes; sometimes the changes are relatively minor and sometimes they are dramatic
  A unity turns ratio phase shifter is a good example with essentially no impedance when the phase shift is zero
  Often modeled with piecewise linear function with impedance correction varying with tap ratio or phase shift
  Next lines give several examples, with format being (phase shift or tap ratio, impedance correction)
    (-60,1), (0,0.01), (60,1)
    (-25,2.43),(0,1),(25,2.43)
    (0.941,0.5), (1.04,1), (1.15,2.45)
    (0.937,1.64), (1,1), (1.1, 1.427)

## Slide 6: Three-Winding Transformers
Three-winding transformers are very common, with the third winding called the tertiary
  The tertiary is often a delta winding
Three-winding transformers have various benefits
  Providing station service
  Place for a capacitor connection
  Reduces third-harmonics
  Allows for three different transmission level voltages
  Better handling of fault current

## Slide 7: Three-Winding Transformers
Usually modeled in the power flow with a star equivalent; the internal “star” bus does not really exist
Star bus is often given a voltage of 1.0 or 999 kV
Impedances calculated using the wye-delta transform can result in negative resistance (about 900 out of 97,000 in EI model)
Image from Power System Analysis and Design, by Glover, Overbye, and Sarma 6th Edition
The winding impedances are measured between the windings with one winding shorted and the other open; for example Z12 is measured from 1 with winding 2 shorted, 3 open

## Slide 8: Three-Winding Transformer Example
Image from Power System Analysis and Design, by Glover, Overbye, and Sarma 6th Edition
Z12 = Z1 + Z2
Z13 = Z1 + Z3
Z23 = Z2 + Z3
Hence
Z1=0.5(Z12+Z13-Z23)
Z2=0.5(Z12+Z23-Z13)
Z3=0.5(Z13+Z23-Z12)

## Slide 9: Three-Winding Transformer Example, cont.
Image from Power System Analysis and Design, by Glover, Overbye, and Sarma 6th Edition

## Slide 10: When Transformers go Bad

## Slide 11: Switched Shunts and SVCs
Switched capacitors and sometimes reactors are widely used at both the transmission and distribution levels to supply or (for reactors) absorb discrete amounts of reactive power
Static var compensators (SVCs) are also used to supply continuously varying amounts of reactive power
In the power flow SVCs are sometimes represented as PV buses with zero real power

## Slide 12: Switched Shunt Control
The status of switched shunts can be handled in an outer loop algorithm, similar to what is done for LTCs and phase shifters
  Because they are discrete they need to regulate a value to a voltage range
Switches shunts often have multiple levels that need to be simulated
Switched shunt control also interacts with the LTC and PV control
The power flow modeling needs to take into account the control time delays associated with the various devices

## Slide 13: Switched Shunt System Design
Because switched shunts tend to have a local impact, there needs to be a coordinated design in their implementation at the transmission level
  Shunt capacitors used to raise the voltage, shunt reactors used to lower the voltage; used with LTCs and gens
Often in the transmission system they are switched manually by a system operator
The size and number of banks depends
  Change in the system voltages caused by bank switching
  The availability of different sizes
  Cost for the associated switchgear and protection system

## Slide 14: Switched Shunt Sizing
A goal with switched shunt sizing is to avoid human irritation caused by excessive changes in lighting
IEEE Std 1453-2015 gives guidance on the percentage of voltage changes as a function of time; Table 3 of the standard suggests keeping the voltage changes below about 3%
We determine analytic methods to calculate this percentage later in the semester
Image from IEEE Std. 1453-2015, “IEEE Recommended Practice for Measurement and Limits of Voltage Fluctuations and Associated Light Flicker on AC Power Systems”

## Slide 15: Dynamic Reactive Capability
Switched shunts are often used to maintain adequate dynamic reactive power from generators and SVCs
FERC Order 827 (from June 2016, titled “Reactive Power Requirements for Non-Synchronous Generation”) states that the power factor of generators should be between 0.95 leading to 0.95 lagging
  Hence the absolute value of the Mvar output of the machines should be no more than 31% of the MW output
  Often a value substantially better for reactive reserves
Switched shunts are used to keep the generator power factor within this range

## Slide 16: Area Interchange Control
The purpose of area interchange control is to regulate or control the interchange of real power between specified areas of the network
Under area interchange control, the mutually exclusive subnetworks, the so-called areas, that make up a power system need to be explicitly represented
These areas may be particular subnetworks of a power grid or may represent various interconnected systems
The specified net power out of each area is controlled by the generators within the area
A power flow may have many more areas than balancing authority areas

## Slide 17: Area Interchange Control
The net power interchange for an area is the algebraic sum of all its tie line real power flows
We denote the real power flow across the tie line from bus k to bus m by Pkm
We use the convention that Pkm > 0 if power leaves node k and Pkm  0 otherwise
Thus the net area interchange Si of area i is positive (negative) if area i exports (imports)
Consider the two areas i and j that are directly connected by the single tie line (k, m) with the node k in area i and the node m in area j

## Slide 18: Net Power Interchange
Then, for the complex power interchange Si, we have a sum in which Pkm appears with a positive sign; for the area j power interchange it appears with a negative sign
Area i
Area j
Pkm
Area i exports Pkm and Area j imports Pkm
k
m

## Slide 19: Net Power Interchange
Since each tie line flow appears twice in the net interchange equations, it follows that if the power system as a distinct areas, then
Consequently, the specification of Si for a collection of (a-1) areas determines the system interchange; we must leave the interchange for one area unspecified
  This is usually (but not always) the area with the system slack bus

## Slide 20: Modeling Area Interchange
Area interchange is usually modeled using an outer loop control
The net generation imbalance for an area can be handled using several different approach
  Specify a single area slack bus, and the entire generation change is picked up by this bus; this may work if the interchange difference is small
  Pick up the change at a set of generators in the area using constant participation factors; each generator gets a share
  Use some sort of economic dispatch algorithm, so how generation is picked up depends on an assumed cost curve
  Min/max limits need to be enforced

## Slide 21: Including Impact on Losses
A change in the generation dispatch can also change the system losses. These incremental impacts need to be included in an area interchange algorithm
We’ll discuss the details of these calculations later in the course when we consider sensitivity analysis

## Slide 22: Area Interchange Example: Seven Bus, Three Area System
PowerWorld Case: B7Flat

## Slide 23: Example Large System Areas
Each oval corresponds to a power flow area with the size proportional to the area’s generation

## Slide 24: Generator Volt/Reactive Control
Simplest situation is a single generator at a bus regulating its own terminal
  Either PV, modeled as a voltage magnitude constraint, or as a PQ with reactive power fixed at a limit value. If PQ the reactive power limits can vary with the generator MW output
Next simplest is multiple generators at a bus. Obviously they need to be regulating the bus to the same voltage magnitude
  From a power flow solution perspective, it is similar to a single generator, with limits being the total of the individual units
  Options for allocation of vars among generators; this can affect the transient stability results

## Slide 25: Generator Voltage Control
This example uses the case PSC_37Bus with a voltage contour. Try varying the voltage setpoint for the generator at PEAR69

## Slide 26: Generator Remote Bus Voltage Control
Next complication is generators at a single bus regulating a remote bus; usually this is the high side of their generator step-up (GSU) transformer
  When multiple generators regulate a single point their exciters need to have a dual input
  This can be implemented in the power flow for the generators at bus j regulating the voltage at bus k by changing the bus j voltage constraint equation to be (however, this does create a zero on the diagonal of the Jacobian)
  Helps with power system voltage stability

## Slide 27: Reactive Power Sharing Options
Different software packages use different approaches for allocating the reactive power; PowerWorld has several options.

## Slide 28: Reactive Power Sharing
In this example, case PSC_37Bus_Varsharing, the two generators at Elm345 are jointly controlling Elms138

## Slide 29: Generator Remote Bus Voltage Control
The next complication is to have the generators at multiple buses doing coordinated voltage control
  Controlled bus may or may not be one of the terminal buses
There must be an a priori decision about how much reactive power is supplied by each bus; example allocations are a fixed percentage or placing all generators at the same place in their regulation range
Implemented by designating one bus as the master; this bus models the voltage constraint
All other buses are treated as PQ, with the equation including a percent of the total reactive power output of all the controlling bus generators

## Slide 30: Remote and Coordinated Var Control Example
Here the generators at Elm345 and the one at Birch69 are jointly controlling the voltage at the Lemon138 bus.
Case is PSC_37Bus_Varsharing_MultipleBuses

## Slide 31: Example of Hourly Voltage Variation Over Time

## Slide 32: Power Flow Topology Processing
Commercial power flow software must have algorithms to determine the number of asynchronous, interconnected systems in the model
  These separate systems are known as Islands
  In large system models such as the Eastern Interconnect it is common to have multiple islands in the base case (one recent EI model had nine islands)
  Islands can also form unexpectedly as a result of contingencies
  Power can be transferred between islands using dc lines
  Each island must have a slack bus

## Slide 33: Power Flow Topology Processing
Anytime a status change occurs the power flow must perform topology processing to determine whether there are either 1) new islands or 2) islands have merged
Determination is needed to determine whether the island is “viable.” That is, could it truly function as an independent system, or should the buses just be marked as dead
  A quite common occurrence is when a single load or generator is isolated; in the case of a load it can be immediately killed; generators are more tricky

## Slide 34: Topology Processing Algorithm
Since topology processing is performed often, it must be quick (order n ln(n))!
Simple, yet quick topology processing algoritm
  Set all buses as being in their own island (equal to bus number)
  Set ChangeInIslandStatus true
  While ChangeInIslandStatus Do
    Go through all the in-service lines, setting the islands for each of the buses to be the smaller island number; if the island numbers are different set ChangeInIslandStatus true
  Determine which islands are viable, assigning a slack bus as necessary
This algorithm does depend on the depth of the system

## Slide 35: Example of Island Formation
Splitting large systems requires a careful consideration of the flow on the island tie-lines as they are opened
This option allows some islands to not have a power flow solution

## Slide 36: Bus Branch versus Node Breaker
Due to a variety of issues during the 1970’s and 1980’s the real-time operations and planning stages of power systems adopted different modeling approaches
Planning
Use simplified bus/branch model
PC approach
Use of files
Stand-alone applications
Real-Time Operations
Use detailed node/breaker model
EMS system as a set of integrated applications and processes
Real-time operating system
Real-time databases
  Entire data sets and software tools developed around these two distinct power system models

## Slide 37: Google View of a 345 kV Substation

## Slide 38: Example of Using a Disconnect to Break Load Current