## Slide 1: ECEN 667 Power System Stability
Lecture 23: Small Signal Stability, Oscillations
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 8
Homework 5 is due Today
Homework 6 is due on Tuesday December 3
Final is at scheduled time here (December 9 from1pm to 3pm)

## Slide 3: Example: Bus 4 SMIB Dialog
On the SMIB dialog, the General Information tab shows information about the two bus equivalent
PowerWorld case B4_SMIB

## Slide 4: Example: Bus 4 SMIB Dialog
On the SMIB dialog, the A Matrix tab shows the Asys matrix for the SMIB generator
In this example A21 is showing

## Slide 5: Example: Bus 4 with GENROU Model
The eigenvalues can be calculated for any set of generator models
The example can be extended by replacing the bus 4 generator classical machine with a GENROU model
  There are now six eigenvalues, with the dominate response coming from the electro-mechanical mode with a frequency of 1.84 Hz, and damping of 6.9%
PowerWorld case B4_SMIB_GENROU

## Slide 6: Relation to the Signal-Based Approaches
The results from the SMIB analysis can be compared with the signal-based approach by applying a short self-clearing fault to disturb the system
This can be done easily in PowerWorld by running the transient stability simulation, looking at the Results from RAM page, right-clicking on the desired signal(s) and selecting Modal Analysis Selected Column.
The next slide shows the results for the Bus 4 Generator rotor angle (which would not be directly observable)

## Slide 7: Bus 4 Generator Rotor Angle
Notice that the main mode, at 1.84 Hz with 7% damping closely matches
Not all modes will be easily observed in all signals

## Slide 8: Example: Bus 4 with GENROU Model and Exciter
Adding an relatively slow EXST1 exciter adds additional states (with KA=200, TA=0.2)
  As the initial reactive power output of the generator is decreased, the system becomes unstable
Case is saved as B4_GENROU_EXST1

## Slide 9: Example: Bus 4 with GENROU Model and Exciter
With Q4 = 25 Mvar the eigenvalues are
And with Q4=0 Mvar the eigenvalues are

## Slide 10: Example: Bus 4 with GENROU Model and Exciter
Graph shows response following a short fault when Q4 is 0 Mvar
This motivates trying to get additional insight into how to increase system damping, which is the goal of modal analysis

## Slide 11: Modal Analysis - Comments
Modal analysis (analysis of small signal stability through eigenvalue analysis) is at the core of SSA software
In Modal Analysis one looks at:
  Eigenvalues
  Eigenvectors (left or right)
  Participation factors
  Mode shape
Power System Stabilizer (PSS) design in a multi-machine context can be done using modal analysis method (we’ll see another method later)
Goal is to determine how the various parameters affect the response of the system

## Slide 12: Eigenvalues, Right Eigenvectors
For an n by n matrix A the eigenvalues of A are the roots of the characteristic equation:
Assume l1…ln as distinct (no repeated eigenvalues).
For each eigenvalue li there exists an eigenvector such that:
vi is called a right eigenvector
If li is complex, then vi has complex entries

## Slide 13: Left Eigenvectors
For each eigenvalue li there exists a left eigenvector wi such that:
Equivalently, the left eigenvector is the right eigenvector of AT; that is,

## Slide 14: Eigenvector Properties
The right and left eigenvectors are orthogonal i.e.
We can normalize the eigenvectors so that:

## Slide 15: Eigenvector Example
Right Eigenvectors

## Slide 16: Eigenvector Example
Left eigenvectors
We would like to make
This can be done in many ways.

## Slide 17: Eigenvector Example
It can be verified that WT=V-1 .
The left and right eigenvectors are used in computing the participation factor matrix.

## Slide 18: Modal Matrices
The deviation away from an equilibrium point can be defined as
If the initial deviation corresponds to a right eigenvector, then the subsequent response is along this eigenvector since

## Slide 19: Modal Matrices
From this equation ( ) it is difficult to determine how parameters in A affect a particular x because of the variable coupling
To decouple the problem first define the matrices of the right and left eigenvectors (the modal matrices)

## Slide 20: Modal Matrices
It follows that
To decouple the variables define z so
Then
Since  is diagonal, the equations are now uncoupled with
So

## Slide 21: Example
Assume the previous system with

## Slide 22: Modal Matrices
Thus the response can be written in terms of the individual eigenvalues and right eigenvectors as
Furthermore with
So z(t) can be written as using the left eigenvectors as
Note, we are requiring that
the eigenvalues be distinct!

## Slide 23: Modal Matrices
We can then write the response x(t) in terms of the modes of the system
So ci is a scalar that represents the magnitude of excitation of the ith mode from the initial conditions

## Slide 24: Numerical example

## Slide 25: Numerical example (contd)

## Slide 26: Numerical example (contd)
Because of the initial condition, the 2nd mode does not get excited

## Slide 27: Mode Shape, Sensitivity and Participation Factors
So we have
x(t) are the original state variables, z(t) are the transformed variables so that each variable is associated with only one mode.
From the first equation the right eigenvector gives the “mode shape” i.e. relative activity of state variables when a particular mode is excited.
For example the degree of activity of state variable xk in vi mode is given by the element Vki of the the right eigenvector matrix V

## Slide 28: Mode Shape, Sensitivity and Participation Factors
The magnitude of elements of vi give the extent of activities of n state variables in the ith mode and angles of elements (if complex) give phase displacements of the state variables with regard to the mode.
The left eigenvector wi identifies which combination of original state variables display only the ith mode.

## Slide 29: Eigenvalue Parameter Sensitivity
To derive the sensitivity of the eigenvalues to the parameters recall Avi = livi; take the partial derivative with respect to Akj by using the chain rule

## Slide 30: Eigenvalue Parameter Sensitivity
This is simplified by noting that by the definition of wi being a left eigenvector
Therefore
Since all elements of are zero, except the kth row, jth column is 1
Thus

## Slide 31: Sensitivity Example
In the previous example we had
Then the sensitivity of l1 and l2 to changes in A are
For example with

## Slide 32: Eigenvalue Parameter Sensitivity
This is simplified by noting that by the definition of wi being a left eigenvector
Therefore
Since all elements of are zero, except the kth row, jth column is 1
Thus

## Slide 33: Participation Factors
The participation factors, Pki, are used to determine how much the kth state variable participates in the ith mode
The sum of the participation factors for any mode or any variable sum to 1
The participation factors are quite useful in relating the eigenvalues to portions of a model

## Slide 34: Participation Factors
For the previous example with Pki = VkiWik and
We get

## Slide 35: PowerWorld SMIB Participation Factors
The magnitudes of the participation factors are shown on the PowerWorld SMIB dialog
The below values are shown for the four bus example with Q4 = 0
Case is saved as B4_GENROU_Sat_SMIB_QZero

## Slide 36: Oscillations
An oscillation is just a repetitive motion that can be either undamped, positively damped (decaying with time) or negatively damped (growing with time)
If the oscillation can be written as a sinusoid then
And the damping ratio is defined as (see Kundur 12.46)
The percent damping is just the damping ratio multiplied by 100; goal is sufficiently positive damping

## Slide 37: Power System Oscillations
Power systems can experience a wide range of oscillations, ranging from highly damped and high frequency switching transients to sustained low frequency (< 2 Hz) inter-area oscillations affecting an entire interconnect
Types of oscillations include
  Transients: Usually high frequency and highly damped
  Local plant: Usually from 1 to 5 Hz
  Inter-area oscillations: From 0.15 to 1 Hz
  Slower dynamics: Such as AGC, less than 0.15 Hz
  Subsynchronous resonance: 10 to 50 Hz (less than synchronous)

## Slide 38: Example Oscillations
The below graph shows an oscillation that was observed during a 1996 WECC Blackout

## Slide 39: Example Oscillations
The below graph shows oscillations on the Michigan/Ontario Interface on 8/14/03

## Slide 40: Fictitious System Oscillation
Movie shows an example of sustained oscillations in an equivalent system

## Slide 41: Forced Oscillations in WECC (from [1])
Summer 2013 24 hour data: 0.37 Hz oscillations observed for several hours. Confirmed to be forced oscillations at a hydro plant from vortex effect.
2014 data: Another 0.5 Hz oscillation also observed. Source points to hydro unit as well. And 0.7 Hz. And 1.12 Hz. And 2 Hz.
Resonance is possible when a system mode is poorly damped and close. Resonance can be observed in model simulations
1. M. Venkatasubramanian, “Oscillation Monitoring System”, June 2015 http://www.energy.gov/sites/prod/files/2015/07/f24/3.%20Mani%20Oscillation%20Monitoring.pdf

## Slide 42: Inter-Area Modes in the WECC
The dominant inter-area modes in the WECC have been well studied
A good reference paper is D. Trudnowski, “Properties of the Dominant Inter-Area Modes in the WECC Interconnect,” 2012
  Four well known modes are NS Mode A (0.25 Hz), NS Mode B (or Alberta Mode), (0.4 Hz), BC Mode (0.6 Hz), Montana Mode (0.8 Hz)
Below figure from paper shows NS Mode A
On May 29, 2012