## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 13: Power Flow Sensitivities
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 7 (the term reliability is now often used instead of security)
First exam average was 86. The answers are posted.
Homework 4 is due on Thursday October 14.
1

## Slide 3: Power Flow Sensitivity Analysis
The idea of power flow sensitivity analysis is to get an estimate of how some set of values would change with respect to a change in a set of control values
  Need to keep in mind which control responses are implicitly modeled, such as P and Q changes at the slack, Q at PV buses
The approach works by linearizing a system about an operating point; its usefulness depends on the validity of this approximation
Sensitivities are widely used in power system analysis, with some algorithms doing sequential linearizations
  They are most valid for real power, less useful for reactive power

## Slide 4: Analysis Example: Available Transfer Capability
The power system available transfer capability or ATC is defined as the maximum additional MW that can be transferred between two specific areas, while meeting all the specified pre- and post-contingency system conditions
ATC impacts measurably the market outcomes and system reliability and, therefore, the ATC values impact the system and market behavior
A useful reference on ATC is Available Transfer Capability Definitions and Determination from NERC, June 1996 (available online)
3

## Slide 5: ATC and Its Key Components
Total transfer capability (TTC )
  Amount of real power that can be transmitted across an interconnected transmission network in a reliable manner, including considering contingencies
Transmission reliability margin (TRM)
  Amount of TTC needed to deal with uncertainties in system conditions; typically expressed as a percent of TTC
Capacity benefit margin (CBM)
  Amount of TTC needed by load serving entities to ensure access to generation; typically expressed as a percent of TTC
4

## Slide 6: ATC and Its Key Components
Uncommitted transfer capability (UTC)
UTC  TTC – existing transmission commitment
Formal definition of ATC is
ATC  UTC – CBM – TRM
We focus on determining Um,n, the UTC from node m to node n
Um,n is defined as the maximum additional MW that can be transferred from node m to node n without violating any limit in either the base case or in any post-contingency conditions
Initially we’ll focus on flow limits; voltage magnitude and voltage stability will be considered later
5

## Slide 7: UTC (or TTC) Evaluation
for the base case j = 0 and each contingency case
j = 1,2 … , J
6
Goal is to load the lines up to their limits, though only when also considering contingencies

## Slide 8: Conceptual Solution Algorithm
Solve the initial power flow, corresponding to the initial system dispatch (i.e., existing commitments); set the change in transfer t(0) = 0, k=0; set step size d; j is used to indicate either the base case (j=0) or a contingency, j= 1,2,3…J
Compute t(k+1) = t(k) + d
Solve the power flow for the new t(k+1)
Check for limit violations: if violation is found set Ujm,n = t(k) and stop; else set k=k+1, and goto 2
7

## Slide 9: Conceptual Solution Algorithm, cont.
This algorithm is applied for the base case (j=0) and each specified contingency case, j=1,2,..J
The final UTC, Um,n is then determined by
This algorithm can be easily performed on parallel processors since each contingency evaluation is independent of the others
8

## Slide 10: Five Bus Example: Reference
PowerWorld Case: B5_DistFact
9

## Slide 11: Five Bus Example: Reference
 |  |  |  |  | ( MW )
 | 1 | 2 | 0 | 6.25 | 150
 | 1 | 3 | 0 | 12.5 | 400
 | 1 | 4 | 0 | 12.5 | 150
 | 2 | 3 | 0 | 12.5 | 150
 | 3 | 4 | 0 | 12.5 | 150
 | 4 | 5 | 0 | 10 | 1,000
10

## Slide 12: Five Bus Example
We evaluate U2,3 using the previous procedure
  Gradually increase generation at Bus 2 and load at Bus 3
We consider the base case and the single contingency with line 2 outaged (between 1 and 3): J = 1
Simulation results show for the base case that
And for the contingency that
Hence
11

## Slide 13: Five Bus: Maximum Base Case Transfer
12

## Slide 14: Five Bus: Maximum Contingency Transfer
13

## Slide 15: Computational Considerations
Obviously such a brute force approach can run into computational issues with large systems
Consider the following situation:
  10 iterations for each case
  6,000 contingencies
  2 seconds to solve each power flow
It will take over 33 hours to compute a single UTC for the specified transfer direction from m to n.
Consequently, there is an acute need to develop fast tools that can provide satisfactory estimates
14

## Slide 16: Sensitivity Problem Formulation
Denote the system state by
Denote the conditions corresponding to the existing commitment/dispatch by s(0), p(0) and f(0) so that
Define the angle difference as
the power flow equations
line real power flow vector
15
The V values are the voltage magnitudes

## Slide 17: Sensitivity Problem Formulation
16
g includes the real and reactive power balance equations

## Slide 18: Sensitivity Problem Formulation
For a small change, p, that moves the injection from p(0) to p(0) + p , we have a corresponding change in the state x with
We then apply a first order Taylor’s series expansion
17

## Slide 19: Sensitivity Problem Formulation
We consider this to be a “small signal” change, so we can neglect the higher order terms (h.o.t.) in the expansion
Hence we should still be satisfying the power balance equations with this perturbation; so
18

## Slide 20: Sensitivity Problem Formulation
Also, from the power flow equations, we obtain
and then just the power flow Jacobian
19

## Slide 21: Sensitivity Problem Formulation
With the standard assumption that the power flow Jacobian is nonsingular, then
We can then compute the change in the line real power flow vector
20

## Slide 22: Sensitivity Comments
Sensitivities can easily be calculated even for large systems
  If p is sparse (just a few injections) then we can use a fast forward; if sensitivities on a subset of lines are desired we could also use a fast backward
Sensitivities are dependent upon the operating point
  They also include the impact of marginal losses
Sensitivities could easily be expanded to include additional variables in x (such as phase shifter angle), or additional equations, such as reactive power flow
21

## Slide 23: Sensitivity Comments, cont.
Sensitivities are used in the optimal power flow; in that context a common application is to determine the sensitivities of an overloaded line to injections at all the buses
In the below equation, how could we quickly get these values?
  A useful reference is O. Alsac, J. Bright, M. Prais, B. Stott, “Further Developments in LP-Based Optimal Power Flow,” IEEE. Trans. on Power Systems, August 1990, pp. 697-711; especially see equation 3.
22

## Slide 24: Sensitivity Example in PowerWorld
Open case B5_DistFact and then Select Tools, Sensitivities, Flow and Voltage Sensitivities
  Select Single Meter, Multiple Transfers, Buses page
  Select the Device Type (Line/XFMR), Flow Type (MW), then select the line (from Bus 2 to Bus 3)
  Click Calculate Sensitivities; this shows impact of a single injection going to the slack bus (Bus 1)
  For our example of a transfer from 2 to 3 the value is the result we get for bus 2 (0.5440) minus the result for bus 3 (-0.1808) = 0.7248
  With a flow of 118 MW, we would hit the 150 MW limit with (150-118)/0.7248 =44.1MW, close to the limit we found of 45MW
23

## Slide 25: Sensitivity Example in PowerWorld
If we change the conditions to the anticipated maximum loading (changing the load at 2 from 118 to 118+44=162 MW) and we re-evaluate the sensitivity we note it has changed little (from -0.7248 to -0.7241)
  Hence a linear approximation (at least for this scenario) could be justified
With what we know so far, to handle the contingency situation, we would have to simulate the contingency, and reevaluate the sensitivity values
  We’ll be developing a quicker (but more approximate) approach next
24

## Slide 26: Linearized Sensitivity Analysis
By using the approximations from the fast decoupled power flow we can get sensitivity values that are independent of the current state. That is, by using the B’ and B’’ matrices
For the real power line flow we can approximate
25

## Slide 27: Linearized Sensitivity Analysis
Also, for each line 
and so,

## Slide 28: Sensitivity Analysis: Recall the Matrix Notation
The series admittance of line  is g +jb and we define
We define the LN incidence matrix
where the component j of ai is nonzero whenever line i is coincident with node j. Hence A is quite sparse, with at most two nonzeros per row

## Slide 29: Linearized Active Power Flow Model
Under these assumptions the change in the real power line flows are given as
The constant matrix is called the injection shift factor matrix (ISF)
28

## Slide 30: Injection Shift Factors (ISFs)
The element in row  and column n of  is called the injection shift factor (ISF) of line  with respect to the injection at node n
  Absorbed at the slack bus, so it is slack bus dependent
Terms generation shift factor (GSF) and load shift factor (LSF) are also used (such as by NERC)
  Same concept, just a variation in the sign whether it is a generator or a load
  Sometimes the associated element is not a single line, but rather a combination of lines (an interface)
Terms used in North America are defined in the NERC glossary (http://www.nerc.com/files/glossary_of_terms.pdf)
29

## Slide 31: ISF Interpretation
is the fraction of the additional 1 MW injection at node n that goes though line 
slack
node
30

## Slide 32: ISF Properties
By definition, depends on the location of the slack bus
By definition, for since the injection and withdrawal buses are identical in this case and, consequently, no flow arises on any line 
The magnitude of is at most 1 since
Note, this is strictly true only for the linear (lossless) case. In the nonlinear case, it is possible that a transaction decreases losses. Hence a 1 MW injection could change a line flow by more than 1 MW.
31

## Slide 33: Five Bus Example Reference
32

## Slide 34: Five Bus ISF, Line 4, Bus 2 (to Slack)
33

## Slide 35: Five Bus Example
The row of A correspond to
the lines and transformers,
the columns correspond to
the non-slack buses (buses 2
to 5); for each line there
is a 1 at one end, a -1 at the
other end (hence an
assumed sign convention!).
Here we put a 1 for the
lower numbered bus, so positive flow is assumed from the lower numbered bus to the higher number
34

## Slide 36: Five Bus Example
35
With bus 1 as the slack, the buses (columns) go for 2 to 5

## Slide 37: Five Bus Example Comments
At first glance the numerically determined value of (128-118)/20=0.5 does not match closely with the analytic value of 0.5455; however, in doing the subtraction we are losing numeric accuracy
  Adding more digits helps (128.40 – 117.55)/20 = 0.5425
The previous matrix derivation isn’t intended for actual computation;  is a full matrix so we would seldom compute all of its values
Sparse vector methods can be used if we are only interested in the ISFs for certain lines and certain buses
36