## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 17:EMSs, SVD, Pseudo Inverse, Equivalents
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Skim Chapters 3, 4 and 5
Starting reading Chapter 8
Homework 5 is due on Thursday Oct 29
1

## Slide 3: Energy Management Systems (EMSs)
EMSs are now used to control most large scale electric grids
EMSs developed in the 1970’s and 1980’s out of SCADA systems
  An EMS usually includes a SCADA system; sometimes called a SCADA/EMS
Having a SE is almost the definition of an EMS. The SE then feeds data to the more advanced functions
EMSs have evolved as the industry as evolved as the industry has evolved, with functionality customized for the application (e.g., a reliability coordinator or a vertically integrated utility)
2

## Slide 4: NERC Reliability Coordinators
Source: www.nerc.com/pa/rrm/TLR/Pages/Reliability-Coordinators.aspx
3

## Slide 5: EEI Member Companies
4

## Slide 6: Electric Coops
5

## Slide 7: Texas Electric Coops
6

## Slide 8: ERCOT Control Center with EMS
7
Source: www.texastribune.org/2016/05/17/texas-market-forces-driving-shift-coal-study-says/

## Slide 9: ERCOT EMS
Slide source: ERCOT, D. Penney, J. Mandavilli, M. Henry, “Loss of SCADA, EMS or LCC”
8

## Slide 10: ERCOT EMS
9

## Slide 11: Aside: Singular Value Decomposition
Traditionally power system analysis has mostly been focused on the sparse matrices associated with the electric grid; there was not much signal analysis
This is rapidly changing as the power industry get more signals and need to extract information from them, with PMUs one example
This data is often presented in the form of a matrix, for example with the rows being sample points
A key technique for extracting information from matrices is known as the singular value decomposition
10

## Slide 12: Aside: Matrix Singular Value Decomposition (SVD)
The SVD is a factorization of a matrix that generalizes the eigendecomposition to any m by n matrix to produce where S is a diagonal matrix of the singular values, and U and V are orthogonal matrices
The singular values are non-negative real numbers that can be used to indicate the major components of a matrix (the gist is they provide a way to decrease the rank of a matrix
A key application is image compression
The original concept is more than
100 years old, but has founds lots of recent applications
11

## Slide 13: Aside: SVD Image Compression Example
Image Source: www.math.utah.edu/~goller/F15_M2270/BradyMathews_SVDImage.pdf
Images can be represented with matrices. When an SVD is applied and only the largest singular values are retained the image is compressed.
12

## Slide 14: Aside: SVD and Principle Component Analysis (PCA)
The previous image compression example demonstrates PCA, which reduces dimensionality
  Extracting the principle components
The principle components are associated with the largest singular values
  This helps to extract the key features of the data and removes redundancy
PCA can be used to do facial recognition
PCA is starting to be more widely used in power system analysis, particularly when doing signal analysis
13

## Slide 15: Aside: An SVD Application, the Pseudoinverse of a Matrix
The pseudoinverse of a matrix generalizes concept of a matrix inverse to an m by n matrix, m >= n
  Specifically this is a Moore-Penrose Matrix Inverse
Notation for the pseudoinverse of A is A+
Satisfies AA+A = A
If A is a square matrix, then A+ = A-1
Quite useful for solving the least squares problem since the least squares solution of Ax = b is x = A+ b
Can be calculated using an SVD
14

## Slide 16: Aside: Pseudoinverse Least Squares Matrix Example
Assume we wish to fit a line (mx + b = y) to three data points: (1,1), (2,4), (6,4)
Two unknowns, m and b; hence x = [m b]T
Setup in form of Ax = b
15

## Slide 17: Aside: Pseudoinverse Least Squares Matrix Example
Doing an economy SVD
Computing the pseudoinverse
In an economy SVD the S matrix has dimensions of m by m if m < n or n by n if n < m
16

## Slide 18: Least Squares Matrix Pseudoinverse Example, cont.
Computing x = [m b]T gives
With the pseudoinverse approach we immediately see the sensitivity of the elements of x to the elements of b
  New values of m and b can be readily calculated if y changes
Computationally the SVD is order mn2+n3 (with n < m)
17

## Slide 19: Power System Equivalents
No electric grid model is ever going to completely represent a real electric grid
  “All models are wrong but some models are useful”
A key modeling consideration is how much of the electric grid to represent
  For large-scale systems the distribution system is usually equivalenced at some point; this has few system level ramifications if it is radial; if it is networked then there are potential issues
  At the transmission level either the full interconnect is represented or it is equivalenced
  In an SE model in large grids (like the Eastern Interconnect) it is always an electrical equivalent
18

## Slide 20: Kron Reduction, Ward Equivalents
For decades power system network models have been equivalenced using the approach originally presented by J.B. Ward in 1949 AIEE paper “Equivalent Circuits for Power-Flow Studies”
  Paper’s single reference is to 1939 book by Gabriel Kron, so this is also known as Kron’s reduction or a Ward equivalent
System buses are partitioned into a study system (s) to be retained and an external system (e) to be eliminated; buses in study system that connect to the external are known as boundary buses
19

## Slide 21: Ward Equivalents
The Ward approach is based on the below relationship
No impact on study, non-boundary buses
Equivalent is created by doing a partial factorization of the Ybus
  Computationally efficient
20

## Slide 22: Other Types of Equivalents
There are many different methods available for creating power system equivalents
  A classic paper is by S. Deckmann, et. al., “Studies on Power System Load Flow Equivalencing,” IEEE Transactions Power App. And Syst., Nov/Dec 1980
  Companion paper covers numerical testing of equivalents
The major equivalencing types are
  Ward-Type Equivalence: this is what we’ll be covering, with the major differences associated with how the generator buses and equivalent loads are represented
  REI Equivalents: All boundary buses connect to one “REI” bus
  Linearized Methods: Linearize about an operating point
  Others: PTDF-based, backbone type
21

## Slide 23: Equivalent System Properties
An equivalent is usually created from a larger model
  In the Eastern Interconnect there are full grid models that are used for wide-area planning, these are equivalenced for real-time usage or more specialized studies
The equivalent is usually smaller and less detailed
  Solves quicker
  Requires less storage
  Requires less up-to-date data
Equivalences contain fictitious elements
  This can make modeling/updating more difficult
The equivalent only approximates the behavior of the original
22

## Slide 24: Study vs External System
The key decision in creating an equivalent is to divide the system into a study portion that is represented in detail, and an external portion that is represented by the equivalent
The two systems are joined at boundary buses, which are part of the study subsystem
How this is done is application specific; for example:
  for real-time use it does not make sense to retain significant portions of the grid for which there is no real-time information
  for contingency analysis the impact of the contingency is localized
  for planning the new system additions have localized impacts
23

## Slide 25: Ward Type Equivalencing
24

## Slide 26: Ward Type Equivalencing Considerations
The Ward equivalent is calculated by doing a partial factorization of the Ybus
  The equivalent buses are numbered before the study buses
  As the equivalent buses are eliminated their first neighbors are joined together
  At the end, many of the boundary buses are connected
  This can GREATLY decrease the sparsity of the system
  Buses with different voltages can be directly connected
25

## Slide 27: Ward Type Equivalencing Considerations
At the end of the Ward process often many of the new equivalent lines have high impedances
  Often there is an impedance threshold, and lines with impedances above this value are eliminated
The equivalent lines may have unusual values, including negative resistances
Load and generation is represented as equivalent current injections or shunts; sometimes these values are converted back to constant power
Consideration needs to be given to loss of reactive support; the equivalent embeds the present load and generation values
26

## Slide 28: B7Flat_Eqv Example
In this example the B7Flat_Eqv case is reduced, eliminating buses 1, 3 and 4. The study system is then 2, 5, 6, 7, with buses 2 and 5 the boundary buses
For ease of comparison system is modeled unloaded
27

## Slide 29: B7Flat_Eqv Example
Original Ybus
28

## Slide 30: B7Flat_Eqv Example
29
Note Yes=Yse' if no phase shifters

## Slide 31: Equivalencing in PowerWorld
Open a case and solve it; then select Edit Mode, Tools, Equivalencing; this displays the Power System Equivalents Form
30
Next step is then to divide the buses into the study system and the external system; buses can be loaded from a text file as well

## Slide 32: Equivalencing in PowerWorld
Then go to the Create The Equivalent page, select the desired options and select Build Equivalent System
31
Maximum impedance lines to retain
’99’ or ‘EQ’ are common circuit values for equivalent lines
Removes equivalenced objects from the oneline
Click to create the equivalent

## Slide 33: Small System Equivalent Example
Example shows the creation of an equivalent for Aggieland37 example
32
Case is Aggieland37_HW5
First example is simple, just removing WHITE138 (bus 3); note TEXAS138 is now directly joined to RELLIS138..

## Slide 34: Small System Equivalent Example
Only bus 3 was removed; the new equivalent line was auto-inserted.
Don’t save the equivalent with the same name as the original, unless you want to lose the original
33

## Slide 35: Small System Equivalent Example
Now remove buses at WHITE138 and TEXAS and RELLIS (1, 3, 12, 40, 41, 44); set Max Per Unit Impedance for Equivalent Lines to 99 (per unit) to retain all lines. Again to an auto- insert to show the equivalent lines.
34

## Slide 36: Small System Equivalent Example
Now set the Max Per Unit Impedance for Equivalent Lines to 2.5.
35

## Slide 37: Large System Example: 70K Case
Original System has 70,000 buses and 71,343 lines
36

## Slide 38: Large System Example: 70K Case
Just retain the Oklahoma Area; now 1591 buses and 1745 lines (deleting ones above 2.5 pu impedance)
37

## Slide 39: Grid Equivalent Examples
A 2016 EI case had about 350 lines with a circuit ID of ’99’ and about 60 with ‘EQ’ (out of a total of 102,000)
  Both WECC and the EI use ’99’ or ‘EQ’ circuit IDs to indicate equivalent lines
  One would expect few equivalent lines in interconnect wide models
A ten year old EI case had about 1633 lines with a circuit ID of ’99’ and 400 with ‘EQ’ (out of a total of 65673)
A ten year old case with about 5000 buses and 5000 lines had 600 equivalent lines
38

## Slide 40: Example: PJM EMS Equivalent
PJM provides information about their EMS model in
  www.pjm.com/-/media/documents/manuals/m03a.ashx
Data here is from the December 2019 (Rev 18) document
39