## Slide 1: ECEN 667 Power System Stability
Lecture 2: Numeric Solution of Differential Equations
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Start reading Chapters 1 and 2 from the book (Chapter 1 is Introduction, Chapter 2 is Electromagnetic Transients)
On campus students consider signing up for the Energy and Power Group seminar on Fridays at 1130am in ETB 1020 (ECEN 681, Section 604)
As noted, we’ll be hosting the North American Power Symposium (NAPS) on Nov 14-16, 2021. If you would like to help with NAPS contact Prof. Kate Davis at katedavis@tamu.edu

## Slide 3: ERCOT EDP Reach, Sept 10
RSVP by today

## Slide 4: PowerWorld Simulator
Class will make extensive use of PowerWorld Simulator and DS. If you do not have a copy of version 22, the free 42 bus student versions are available for download at
http://www.powerworld.com/gloveroverbyesarma
Start getting familiar with this package, particularly the power flow basics. Stability aspects will be covered in class
Free training material is available at
http://www.powerworld.com/training/online-training

## Slide 5: Modeling Cautions!
"All models are wrong but some are useful," George Box, Empirical Model-Building and Response Surfaces, (1987, p. 424)
  Models are an approximation to reality, not reality, so they always have some degree of approximation
  Box went on to say that the practical question is how wrong to they have to be to not be useful
A good part of engineering is deciding what is the appropriate level of modeling, and knowing under what conditions the model will fail
Always keep in mind what problem you are trying to solve!

## Slide 6: Static versus Dynamic Analysis
Statics versus dynamics appears in many fields
An equilibrium point is a point at which the model is not changing
  Real systems are always changing, but over the time period of interest an unchanging system can be a useful approximation
Static analysis looks at how the equilibrium points change to a change in the model
  Power system example is power flow
Dynamic analysis looks at how the system responds over time when it is perturbed away from an equilibrium point
  Power system example is transient stability

## Slide 7: Slow versus Fast Dynamics
Key analysis question in setting up and solving models is to determine the time frame of interest
Values that change slowing (relative to the time frame of interest) can be assumed as constant
  Power flow example is the load real and reactive values are assumed constant (sometimes voltage dependence is included)
Values that change quickly (relative to the time frame of interest) can be assumed to be algebraic
  A generator's terminal voltage in power flow is an algebraic constraint, but not in transient stability
  In power flow and transient stability the network power balance equations are assumed algebraic

## Slide 8: Dynamics Example 1
1996: Transient Stability Model Errors Lead to Blackouts

## Slide 9: Dynamics Example: August 14 Blackout
Image from August 14, 2003 Blackout Final Report, energy.gov, Figure 6.26
8

## Slide 10: Dynamics Example 3
Source: Arizona-Southern California Outages on September 8, 2011 Report, FERC and NERC,April 2012
We’ve come a long ways since 1996 towards improved simulations. Still, a finding from the 2011 Blackout is the simulations didn’t match the actual system response and need to be improved.

## Slide 11: Models and Their Parameters
Models and their parameters are often tightly coupled
  The parameters for a particular model might have been derived from actual results on the object of interest
Changing the model (even correcting an "incorrect" simulation implementation) can result in unexpected results!
Using a more detailed simulation approach without changing the model can also result in incorrect results
  More detailed models are not necessarily more accurate

## Slide 12: Positive Sequence versus Full Three-Phase
Large-scale electrical systems are almost exclusively three-phase. Common analysis tools such as power flow and transient stability often assume balanced operation
  This allows modeling of just the positive sequence though full three-phase models are sometimes used particularly for distribution systems
  Course assumes knowledge of sequence analysis
Other applications, such as electromagnetic transients (commonly known as electromagnetic transients programs [EMTP]) consider the full three phase models

## Slide 13: Power Flow Versus Dynamics
The power flow is used to determine a quasi steady-state operating condition for a power system
  Goal is to solve a set of algebraic equations g(x) = 0
  Models employed reflect the steady-state assumption, such as generator PV buses, constant power loads, LTC transformers
Dynamic analysis is used to determine how the system changes with time, usually after some disturbance perturbs it away from a quasi-steady state equilibrium point

## Slide 14: Example: Transient Stability
Transient stability is used to determine whether following a disturbance (contingency) the power system returns to a steady-state operating point
  Goal is to solve a set of differential and algebraic equations, dx/dt = f(x,y), g(x,y) = 0
  Starts in steady-state, and hopefully returns to steady-state.
  Models reflect the transient stability time frame (up to dozens of seconds), with some values assumed to be slow enough to hold constant (LTC tap changing), while others are still fast enough to treat as algebraic (synchronous machine stator dynamics, voltage source converter dynamics).

## Slide 15: Interactive Simulation: PowerWorld Dynamics Studio (DS)

## Slide 16: Power System Stability Terms
Terms continue to evolve, but a good reference is [1]; image shows Figure 4 from this reference
[1] IEEE/PES Power System Dynamic Performance Committee, “Stability definitions and characterization of dynamic behavior in systems with high penetration of power electronic interfaced technologies”, PES-TR77, April 2020
15

## Slide 17: Physical Structure Power System Components
P. Sauer and M. Pai, Power System Dynamics and Stability

## Slide 18: Physical Structure Power System Components
Generator
Voltage Control
P, Q
Network
Network control
Loads
Load control
Fuel
Source
Supply control
Furnace and Boiler
Pressure control
Turbine
Speed control
V, I
Torque
Steam
Fuel
Electrical System
Mechanical System
Governor
Machine
Exciter
Load
Char.
Load
Relay
Line
Relay
Stabilizer

## Slide 19: Differential Algebraic Equations
Many problems, including many in the power area, can be formulated as a set of differential, algebraic equations (DAE) of the form
A power example is transient stability, in which f represents (primarily) the generator dynamics, and g (primarily) the bus power balance equations
We'll initially consider the simpler problem of just

## Slide 20: Ordinary Differential Equations (ODEs)
Assume we have a problem of the form
This is known as an initial value problem, since the initial value of x is given at some time t0
  We need to determine x(t) for future time
  Initial value, x0, must be either be given or determined by solving for an equilibrium point, f(x) = 0
  Higher-order systems can be put into this first order form
Except for special cases, such as linear systems, an analytic solution is usually not possible – numerical methods must be used

## Slide 21: Equilibrium Points
An equilibrium point x* satisfies
An equilibrium point is stable if the response to a small disturbance remains small
  This is known as Lyapunov stability
  Formally, if for every e > 0, there exists a d = d(e) > 0 such that if x(0) – x* < d, then x(t) – x* < e for t  0
An equilibrium point has asymptotic stability if there exists a d > 0 such that if x(0) – x* < d, then

## Slide 22: Power System Application
A typical power system application is to assume the power flow solution represents an equilibrium point
Back solve to determine the initial state variables, x(0)
At some point a contingency occurs, perturbing the state away from the equilibrium point
Time domain simulation is used to determine whether the system returns to the equilibrium point

## Slide 23: Initial value Problem Examples

## Slide 24: Numerical Solution Methods
Numerical solution methods do not generate exact solutions; they practically always introduce some error
  Methods assume time advances in discrete increments, called a stepsize (or time step), Dt
  Speed accuracy tradeoff: a smaller Dt usually gives a better solution, but it takes longer to compute
  Numeric roundoff error due to finite computer word size
Key issue is the derivative of x, f(x) depends on x, the value we are trying to determine
A solution exists as long as f(x) is continuously differentiable

## Slide 25: Numerical Solution Methods
There are a wide variety of different solution approaches, we will only touch on several
One-step methods: require information about solution just at one point, x(t)
  Forward Euler
  Runge-Kutta
Multi-step methods: make use of information at more than one point, x(t), x(t-Dt), x(t-D2t)…
  Adams-Bashforth
Predictor-Corrector Methods: implicit
  Backward Euler

## Slide 26: Error Propagation
At each time step the total round-off error is the sum of the local round-off at time and the propagated error from steps 1, 2 , … , k − 1
An algorithm with the desirable property that local round-off error decays with increasing number of steps is said to be numerically stable
Otherwise, the algorithm is numerically unstable
Numerically unstable algorithms can nevertheless give quite good performance if appropriate time steps are used
  This is particularly true when coupled with algebraic equations

## Slide 27: Forward Euler’s Method
The simplest technique for numerically integrating such equations is known as the Euler's Method (sometimes the Forward Euler's Method)
Key idea is to approximate
In general, the smaller the Dt, the more accurate the solution, but it also takes more time steps

## Slide 28: Euler’s Method Algorithm

## Slide 29: Euler’s Method Example 1

## Slide 30: Euler’s Method Example 1, cont’d
t | xactual(t) | x(t) Dt=0.1 | x(t) Dt=0.05
0 | 10 | 10 | 10
0.1 | 9.048 | 9 | 9.02
0.2 | 8.187 | 8.10 | 8.15
0.3 | 7.408 | 7.29 | 7.35
… | … | … | …
1.0 | 3.678 | 3.49 | 3.58
… | … | … | …
2.0 | 1.353 | 1.22 | 1.29

## Slide 31: Euler’s Method Example 2

## Slide 32: Euler's Method Example 2, cont'd

## Slide 33: Euler's Method Example 2, cont'd
t | x1actual(t) | x1(t) Dt=0.25
0 | 1 | 1
0.25 | 0.9689 | 1
0.50 | 0.8776 | 0.9375
0.75 | 0.7317 | 0.8125
1.00 | 0.5403 | 0.6289
… | … | …
10.0 | -0.8391 | -3.129
100.0 | 0.8623 | -151,983
Since we know from the exact solution that x1 is bounded between -1 and 1, clearly the method is numerically unstable

## Slide 34: Euler's Method Example 2, cont'd
Dt | x1(10)
actual | -0.8391
0.25 | -3.129
0.10 | -1.4088
0.01 | -0.8823
0.001 | -0.8423
Below is a comparison of the solution values for x1(t)
at time t = 10 seconds

## Slide 35: Second Order Runge-Kutta Method
Runge-Kutta methods improve on Euler's method by evaluating f(x) at selected points over the time step
Simplest method is the second order method in which
That is, k1 is what we get from Euler's; k2 improves on this by reevaluating at the estimated end of the time step

## Slide 36: Second Order Runge-Kutta Algorithm
t = 0, x(0) = x0, Dt = step size
While t  tfinal Do
k1 = Dt f(x(t))
k2 = Dt f(x(t) + k1)
x(t+Dt) = x(t) + ( k1 + k2)/2
t = t + Dt
End While

## Slide 37: RK2 Oscillating Cart
Consider the same example from before the position of a cart attached to a lossless spring. Again, with initial conditions of x1(0) =1 and x2(0) = 0, the analytic solution is x1(t) = cos(t)
With Dt=0.25 at t = 0

## Slide 38: RK2 Oscillating Cart

## Slide 39: Comparison
The below table compares the numeric and exact solutions for x1(t) using the RK2 algorithm
time | actual x1(t) | x1(t) with RK2 Dt=0.25
0 | 1 | 1
0.25 | 0.9689 | 0.969
0.50 | 0.8776 | 0.876
0.75 | 0.7317 | 0.728
1.00 | 0.5403 | 0.533
10.0 | -0.8391 | -0.795
100.0 | 0.8623 | 1.072

## Slide 40: Comparison of x1(10) for varying Dt
The below table compares the x1(10) values for different values of Dt; recall with Euler's with Dt=0.1 was -1.41 and with 0.01 was -0.8823
Dt | x1(10)
actual | -0.8391
0.25 | -0.7946
0.10 | -0.8310
0.01 | -0.8390
0.001 | -0.8391

## Slide 41: RK2 Versus Euler's
RK2 requires twice the function evaluations per iteration, but gives much better results
With RK2 the error tends to vary with the cube of the step size, compared with the square of the step size for Euler's
The smaller error allows for larger step sizes compared to Eulers

## Slide 42: Fourth Order Runge-Kutta
Other Runge-Kutta algorithms are possible, including the fourth order