## Slide 1: ECEN 460 Power System Operation and Control
Lecture 10: Synchronous Machine Modeling
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
After the test read Chapter 6.7 to 6.11
HW 4 is 6.9, 6.12, 6.18, 6.25
  It should be done before the first exam, but need not be turned in.
Lowest two homework scores will be dropped
First exam is Thursday Oct 5 in class; one of my old exams is posted for reference; closed book, closed notes, one 8.5 by 11 inch note sheet allowed; calculators allowed
  Exam covers up to Sept 28 lecture, except not the synchronous machine material

## Slide 3: Rotation Speed and Two Main Types of Synchronous Machines
Machines may have multiple pole pairs to spin at speeds slower than the electrical frequency
Round Rotor
  Air-gap is constant, used with higher speed machines
Salient Rotor (often called Salient Pole)
  Air-gap varies circumferentially
  Used with many pole, slower machines such as hydro

## Slide 4: Synchronous Machine Rotors
Rotors are essentially electromagnets
Image Source: Dr. Gleb Tcheslavski, ee.lamar.edu/gleb/teaching.htm
Two pole (P) round rotor
Six pole salient
rotor

## Slide 5: Synchronous Machine Rotors
Image Source: Dr. Gleb Tcheslavski, ee.lamar.edu/gleb/teaching.htm
High pole salient rotor
Shaft
Part of exciter, which is used to control the field current

## Slide 6: Synchronous Machine Stators
Image Source: Book, Beginning of Chapter 8 Photo

## Slide 7: Synchronous Generators
Image Source: Book, Beginning of Chapter 11 Photo

## Slide 8: Brief Coverage of Magnetics
Ampere’s circuital law:

## Slide 9: Magnetic Flux Density
Magnetic fields are usually measured in terms of flux density
Notes: 8

## Slide 10: Magnetic Flux
Notes: 9

## Slide 11: Relative Flux Density Values
Earth’s magnetic field is between 30 and 70 mT (0.3 to 0.7 gauss)
A refrigerator magnet might have 0.005 T
A commercial neodymium magnet might be 1 T
A magnetic resonance imaging (MRI) machine would be between 1 and 3 T
Strong lab magnets can be 10 T
Frogs can be levitated at 16 T (see www.ru.nl/hfml/research/levitation/diamagnetic)

## Slide 12: Flux linkages and Faraday’s law
Notes: 11

## Slide 13: Inductance
For a linear magnetic system, that is one where
B = m H
we can define the inductance, L, to be
the constant relating the current and the flux
linkage
l = L i
where L has units of Henrys (H)
Notes: 12

## Slide 14: Inductance Example
Calculate the inductance of an N turn coil wound tightly on a torodial iron core that has a radius of R and a cross-sectional area of A. Assume
  all flux is within the coil
  all flux links each turn

## Slide 15: Inductance Example, cont’d
Let N=100, A= 0.0006 m2, R=0.03 m, mr=1000; then L is 0.04 H;

## Slide 16: Creating a Voltage in an Open-Circuited Generator
With zero stator current, the only flux is due to the field current
When the generator is at standstill, the flux linking each coil depends on its angle relative to the rotor’s position (and hence the field winding)
  The three phases are physically shifted by 120 degrees from each other
The maximum flux depends on the field current

## Slide 17: Creating a Voltage in an Open-Circuited Generator
No voltage is generated at standstill
Now assume the rotor is spinning at a uniform rate, w = 2pf, so

## Slide 18: Creating a Voltage in an Open-Circuited Generator
Then by Faraday’s law a voltage is induced

## Slide 19: Creating a Voltage in an Open-Circuited Generator
For a linear magnetic circuit we can also write this as proportional to field current
The negative sign could be removed with a change in the assumed polarity

## Slide 20: Magnetic Saturation and Hysteresis
A linear magnetic circuit assumes the flux density B is always proportional to current, but real magnetic materials saturate
Image Source: en.wikipedia.org/wiki/Saturation_(magnetic)
Magnetization curves of 9 ferromagnetic materials, showing saturation. 1.Sheet steel, 2.Silicon steel, 3.Cast steel, 4.Tungsten steel, 5.Magnet steel, 6.Cast iron, 7.Nickel, 8.Cobalt, 9.Magnetite; highest saturation materials can get to around 2.2 or 2.3T
H is proportional to current

## Slide 21: Magnetic Saturation and Hysteresis
Magnetic materials also exhibit hysteresis, so there is some residual magnetism when the current goes to zero; design goal is to reduce the area enclosed by the hysteresis loop
Image source: www.nde-ed.org/EducationResources/CommunityCollege/MagParticle/Graphics/BHCurve.gif
To minimize the amount of magnetic material, and hence cost and weight, electric machines are designed to operate close to saturation

## Slide 22: Frequency Impacts
Assuming no saturation, the generated voltage is then proportional to frequency
To create the same voltage with less flux, we just need to increase the frequency; this is why aircraft operate at a higher frequency (e.g., 400 Hz)
When controlling motors with variable frequency, common control is to use constant volt/Hz, preventing saturation

## Slide 23: Synchronous Machines with Output Current
When operating with an output current, the terminal voltage is not equal to the internally generated voltage
This is due to several factors
  Resistance in the stator windings
  Self-inductance in the stator windings
  Distortion of the air-gap magnetic field due to the stator current; that is, the stator current induces a magnetic field
  Salient pole characteristics of the machine
The stator reactance is called the synchronous reactance, XS, and is sometimes broken into two parts
Xl is due to the winding self inductance

## Slide 24: A Synchronous Machine Model
This gives us the following per phase model, which can be helpful in considering how the steady-state real and reactive output of the machine changes with changes in the field current
This model is not particularly good for saturation and understanding the generator’s dynamic response, something we’ll revisit in Chapter 11

## Slide 25: Synchronous Machine Testing to Determine Its Parameters
These synchronous machine parameters can be determined from two tests (which we’ll do in Lab 4)
  Open-circuit test: measure the machine’s response when there is no load, and the field current is gradually changed
  Short-circuit test: measure the machine’s response when it is operated at rated speed and its terminals are short-circuited

## Slide 26: Lab 4 and 5 Setup
We’ll be using a dc machine (which is speed controllable) to drive a synchronous generator. In lab 4 we’ll be doing open-circuit and short-circuit tests to determine its parameters
In the experiment you’ll be measuring line-to-line values, which are sqrt(3) times the line-to-neutral values

## Slide 27: Open-Circuit Characteristic (OCC)
The open-circuit characteristic (OCC) can be derived by gradually changing the field current when operating at a fixed frequency (e.g., synchronous speed)
  Hysteresis needs to be considered when making field current adjustments
Because there is no stator current, the internal voltage can be directly measured at the terminals
We’ll be using phasor values here

## Slide 28: Short-Circuit Test
The short-circuit characteristic measures the relationship between the field current and the terminal current
With the model we get
Since usually XS >> RA, so
This curve is almost linear since there is little saturation because the fluxes in the machine tend to cancel.

## Slide 29: Short-Circuit Test, cont.
However, in doing this test we cannot directly measure EA and of course the terminal voltage is now zero during the short-circuit.
One approach is to approximate it as

## Slide 30: Short-Circuit Test, cont.
This approach is accurate up to the point of saturation. An alternative approach is to substitute the equivalent air-gap voltage instead of the VOCC value.
  This is commonly called the unsaturated synchronous reactance, Xu
The amount of saturation depends on loading; in large generators saturation is explicitly modeled

## Slide 31: Measuring RA
The winding resistance can be calculated at standstill by applying a small dc voltage to two of the terminals, and then measuring the dc current
Or one could just use an ohmmeter

## Slide 32: Operating Synchronous Machines Under Load
We’ve seen that the terminal voltage of a synchronous machine can be controlled by adjusting its field voltage (and hence field current)
Large generators have a number of automatic control systems, including one called an exciter to keep the terminal voltage or other voltage at a specified value
Small machines might operate with a constant field current

## Slide 33: Operating Synchronous Machines Under Load with a Constant Field
If the field voltage and hence field current are assumed constant, and the speed is assumed constant (which in practice would be controlled by a governor, which we’ll address in Chapter 12), then the internal voltage can be assumed to be constant
  This is what we’ll be assuming in Experiment 5
How the voltage varies with loading is then given by

## Slide 34: Operating Synchronous Machines Under Load with a Constant Field
To help gain insight, we’ll neglect the usually small RA so then
  Arbitrarily we can set the angle of VT to zero
If the load has a lagging power factor then internal voltage magnitude is higher
If leading pf then internal voltage is lower than the terminal voltage

## Slide 35: Operating Synchronous Machines Under Load with a Constant Field
With RA neglected, the power out of the machine is given by
d is called the torque angle; in general it is the angle difference between the internal voltage angle and the terminal voltage angle

## Slide 36: Example
A 200 kVA, 480 V (line-to-line), 60 Hz, Y-connected generator with a rated field voltage of 5A was tested with the following results
  VT,LL = 540 V at rated field current
  IA,SC = 300 A at rated field current
  When disconnected, a dc voltage of 10 V is applied to two of the terminals, giving a current of 25 A
  Find the model

## Slide 37: Example, cont.
The internal, per phase voltage is
The synchronous reactance at the rated field current is
If we wished to include the impact of RA it would be

## Slide 38: Example, cont.
Now assume a three-phase, wye-connected load is attached to its terminal with Z = 420 Ω. The field current is adjusted so the line-to-line terminal voltage is 480 V and the generator is operated at 60 Hz. What is the internal voltage, and what is the total power delivered to the load? Use XS = 1.04 Ω. Then repeat with Z = 4-20 Ω.

## Slide 39: Example, cont.
With Z = 420 Ω
With Z = 4-20 Ω

## Slide 40: Quick Coverage of DC Machines
Prior to widespread use of machine drives, dc motors had a important advantage of easy speed control
  Example is a model railroad
On the stator a dc machine has either a permanent magnet or a single concentrated winding
  With winding field voltage is Vf and field current is If
Rotor (armature) currents are supplied through brushes and commutator

## Slide 41: Types of DC Machines
If there is a field winding (i.e., not a permanent magnet machine) then the machine could be connected in the following ways
  Separately-excited: Field and armature windings are connected to separate power sources
    For an exciter, control is provided by varying the field current (which is stationary), which changes the armature voltage
  Series-excited: Field and armature windings are in series
  Shunt-excited: Field and armature windings are in parallel

## Slide 42: Quick Coverage of DC Machines
In a machine with a field winding the equations are
In steady-state these can be simplified to
In a shunt-connected machine, VT = VF so
G is a machine constant, wm is its speed