## Slide 1: ECEN 460 Power System Operation and Control
Lecture 15: Economic Dispatch
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Finish reading Chapter 6
Homework 5 is due Tuesday Oct 24
Homework 6 is 6.58, 6.59, 6.60, 6.62, 6.63; it is due on Tuesday Oct 31
The TAs will have office hours in WEB 115 to help you finish the lab

## Slide 3: Generation Dispatch
Since the load is variable and there must be enough generation to meet the load, almost always there is more generation capacity available than load
Optimally determining which generators to use can be a complicated task due to many different constraints
  For generators with low or no cost fuel (e.g., wind and solar PV) it is “use it or lose it”
  For others like hydro there may be limited energy for the year
  Some fossil has shut down and start times of many hours
Economic dispatch looks at the best way to instantaneously dispatch the generation
2

## Slide 4: Generator types
Traditionally utilities have had three broad groups of generators
  baseload units: large coal/nuclear; always on at max.
  midload units: smaller coal that cycle on/off daily
  peaker units: combustion turbines used only for several hours during periods of high demand
Wind and solar PV can be quite variable; usually they are operated at max. available power
3

## Slide 5: Utility Scale Generator Capacity Additions in the US
4

## Slide 6: US Electricity Generation by Fuel Type
Source: www.eia.gov/totalenergy/data/monthly/pdf/sec7_4.pdf
In first half of 2017, wind was 7.2% and solar was 1.3%

## Slide 7: Distribution of Wind Power Plants
6

## Slide 8: The Challenge of Wind Dispatch
Image shows wind output for a month in California by hour and day
Source: www.megawattsf.com/gridstorage/gridstorage.htm

## Slide 9: Thermal versus Hydro Generation
The two main types of generating units are thermal and hydro, with wind rapidly growing
For hydro the fuel (water) is free but there may be many constraints on operation
  fixed amounts of water available
  reservoir levels must be managed and coordinated
  downstream flow rates for fish and navigation
Hydro optimization is typically longer term (many months or years)
In 460 we will concentrate on thermal units and some wind, looking at short-term optimization
8

## Slide 10: Block Diagram of Thermal Unit
To optimize generation costs we need to develop
cost relationships between net power out and operating
costs. Between 2-6% of power is used within the
generating plant; this is known as the auxiliary power
9

## Slide 11: Modern Coal Plant
Source: Masters, Renewable and Efficient Electric Power Systems, 2004
10

## Slide 12: Turbine for Nuclear Power Plant
Source: http://images.pennnet.com/articles/pe/cap/cap_gephoto.jpg
11

## Slide 13: Basic Gas Turbine
Most common fuel is natural gas
Typical efficiency is around 30 to 35%
12

## Slide 14: Combined Cycle Power Plant
Efficiencies of up to 60% can be achieved, with even higher values when the steam is used for heating. Fuel is usually natural gas
13

## Slide 15: Generator Cost Curves
Generator costs are typically represented by up to four different curves
  input/output (I/O) curve
  fuel-cost curve
  heat-rate curve
  incremental cost curve
For reference
  1 Btu (British thermal unit) = 1054 J
  1 MBtu = 1x106 Btu
  1 MBtu = 0.293 MWh
  3.41 Mbtu = 1 MWh
14

## Slide 16: I/O Curve
The IO curve plots fuel input (in MBtu/hr) versus net MW output.
15

## Slide 17: Fuel-cost Curve
The fuel-cost curve is the I/O curve scaled by fuel cost. A typical cost for coal is $ 1.70/Mbtu.
16

## Slide 18: Heat-rate Curve
Plots the average number of MBtu/hr of fuel input needed per MW of output.
Heat-rate curve is the I/O curve scaled by MW
Best for most efficient units are
around 9.0
17

## Slide 19: Incremental (Marginal) cost Curve
Plots the incremental $/MWh as a function of MW.
Found by differentiating the cost curve
18

## Slide 20: Mathematical Formulation of Costs
Generator cost curves are usually not smooth. However the curves can usually be adequately approximated using piece-wise smooth, functions.
Two representations predominate
  quadratic or cubic functions
  piecewise linear functions
In 460 we'll assume a quadratic presentation
19

## Slide 21: Coal Usage Example 1
A 500 MW (net) generator is 35% efficient. It is being supplied with Western grade coal, which costs $1.70 per MBtu and has 9000 Btu per pound. What is the coal usage in lbs/hr? What is the cost?
20

## Slide 22: Coal Usage Example 2
Assume a 100W lamp is left on by mistake for 8 hours, and that the electricity is supplied by the previous coal plant and that transmission and distribution losses are 20%. How coal has been used?
21

## Slide 23: Incremental Cost Example
22

## Slide 24: Incremental Cost Example, cont'd
23

## Slide 25: Economic Dispatch: Formulation
The goal of economic dispatch is to determine the generation dispatch that minimizes the instantaneous operating cost, subject to the constraint that total generation = total load + losses
Initially we'll
ignore generator
limits and the
losses
24

## Slide 26: Unconstrained Minimization
This is a minimization problem with a single equality constraint
For an unconstrained minimization a necessary (but not sufficient) condition for a minimum is the gradient of the function must be zero,
The gradient generalizes the first derivative for multi-variable problems:
25

## Slide 27: Minimization with Equality Constraint
When the minimization is constrained with an equality constraint we can solve the problem using the method of Lagrange Multipliers
Key idea is to modify a constrained minimization problem to be an unconstrained problem
26

## Slide 28: Economic Dispatch Lagrangian
27

## Slide 29: Economic Dispatch Example
28

## Slide 30: Economic Dispatch Example, cont’d
29

## Slide 31: Lambda-Iteration Solution Method
The direct solution only works well if the incremental cost curves are linear and no generators are at their limits
A more general method is known as the lambda-iteration
  the method requires that there be a unique mapping between a value of lambda and each generator’s MW output
  the method then starts with values of lambda below and above the optimal value, and then iteratively brackets the optimal value
30

## Slide 32: Lambda-Iteration Algorithm
31

## Slide 33: Lambda-Iteration: Graphical View
In the graph shown below for each value of lambda
there is a unique PGi for each generator. This
relationship is the PGi() function.
32

## Slide 34: Lambda-Iteration Example
33

## Slide 35: Lambda-Iteration Example, cont’d
34

## Slide 36: Lambda-Iteration Example, cont’d
35

## Slide 37: Lambda-Iteration Example, cont’d
36

## Slide 38: Generator MW Limits
Generators have limits on the minimum and maximum amount of power they can produce
Often times the minimum limit is not zero. This represents a limit on the generator’s operation with the desired fuel type
Because of varying system economics usually many generators in a system are operated at their maximum MW limits.
37

## Slide 39: Lambda-Iteration with Gen Limits
38