## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 15: August 14, 2003 Blackout
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 11
Start reading Chapter 9
Homework 5 is due on Oct 27, 2022

## Slide 3: Going Back in Time
The August 14th 2003 blackout is rapidly moving from being a “recent event” into history; yet it still has much to teach us.
This talk is about the past and the future: what can we learn from the past to help us prepare for the future
  But not so much about what are the immediate lessons from the Blackout since many recommendations have already been put into practice.
The blackout final report is very readable and available by googling “August 14 2003 Blackout Report”
2

## Slide 4
In contrasting numbers, the August 14 2003 Blackout hit about 50 million people, while Hurricane
Irene (2011) caused power outages affecting perhaps seven or eight million.
3

## Slide 5: August 14, 2003 Hoax Image
This image was widely circulated immediately after the blackout, even appearing for a time on a DOE website. It was quickly shown to be a hoax. What might immediately give it away?
4

## Slide 6: Actual Before and After Images
5

## Slide 7: My Favorite August 14, 2003 Cartoon
6

## Slide 8: Causes of the Blackout
Blackout Final Report listed four causes
  FirstEnergy (FE) did not understand inadequacies of their system, particularly with respect to voltage instability.
  Inadequate situational awareness by FE
  FE failed to adequately manage their tree growth
  Failure of the grid reliability organizations (primarily MISO) to provide effective diagnostic support
Human/cyber interactions played a key role
7

## Slide 9: We’ve Come Quite a Ways Since 2003
Report included 46 recommendations, many of which have dramatically changed the operation of the interconnected power grid
  Thirteen were focused on physical and cyber security
Focus of talk is what can 8/14/03 teach us to help with the grid in 2022
Need to keep in mind economic impact of 8/14/03 was above $5 billion; yearly impact of blackouts could be above $100 billion
8

## Slide 10: First Energy Control Center, More Recent (2013)
Image Source: www.wksu.org/news/story/365
9

## Slide 11: My Involvement in Blackout Investigation
I spend a lot of time talking to reporters on 8/14 to 8/16, before I knew what happened
Tasked by DOE to do onsite visit to FE on 8/19 to 8/21 with Doug Wiegmann; did similar visit to MISO the next week.
Did return visit in Oct
Many folks played far larger roles; I was only involved extensively early on
10

## Slide 12: Footprints of Reliability Coordinators in Midwest
11
In 2003 the Ohio portion of First Energy was in MISO; they have since moved to being in PJM.

## Slide 13: August 13, 2003
It is important to realize that immediately before the blackout few people thought the system was on the verge of a catastrophe.
NERC 2003 Summer Assessment did not list Ohio as an area of particular concern
NERC 2003 Summer Assessment is available at http://www.nerc.com/files/summer2003.pdf
12

## Slide 14: August 14, 2003: Pre-blackout (before 14:30 EDT)
It had mostly been a normal summer day at First Energy
  Most generation was available though the 883 MW Davis-Besse Nuclear unit was on a long-term outage
  At 13:31 EDT the Eastlake 5 unit (a 597 MW plant on Lake Erie) tripped when the operator tried to up is reactive output, but this was not seen as a severe event
It had been a busy day at MISO, with their reliability coordinators dealing with a relatively small outage in Indiana around noon
  Their state estimator failed at 1215 EDT but no one know this
13

## Slide 15: Cinergy Bedford-Columbus 345 kV Line Tree Contact at 12:08 EDT
14

## Slide 16: Trees were Finally “Trimmed” Two Months Later
15

## Slide 17: At 14:27 EDT Star-South Canton 345 kV Line Trips and Recloses
Star-South Canton is a tie between AEP & FE
FE missed seeing this event since their alarms had hung several minutes earlier (14:14)
    Line was back in service so it appeared normal in SCADA
    FE IT folks knew about computer problems
AEP called FE at 14:32 to check on event; FE says they saw nothing. A repeat call by AEP to FE at 15:19 also discusses event indicating ground current was detected.
16

## Slide 18: Estimated High Level Voltage Profile at 15:00 EDT
17

## Slide 19: Estimated Flows in Northeast Ohio at 15:00 EDT on August 14th 2003
Chamberlin-Harding
345 kV Line trips at 15:05, an event
that was missed by
both FE and MISO
18

## Slide 20: Estimated Flows in Northeast Ohio at 15:06 EDT
19

## Slide 21: Line Outage Distribution Factors (LODFs)
LODFs are used to approximate the change in the flow on one line caused by the outage of a second line
  Typically they are only used to determine the change in the MW flow
  LODFs are used extensively in real-time operations
  LODFs are state-independent (calculated using dc power flow approximations) but do dependent on the assumed network topology
  Below value tells change of real power flow on line  for the assumed outage of line k; ƒk0 is (obviously) pre-contingent
20

## Slide 22: Flowgates
The real-time loading of the power grid is accessed via “flowgates”
A flowgate “flow” is the real power flow on one or more transmission element for either base case conditions or a single contingency
  Contingent flows are determined using LODFs
Flowgates can be used as proxies for other types of limits, such as voltage or stability limits
Flowgates in 2003 were calculated using a spreadsheet
21

## Slide 23: Flowgate #2265
Flowgate 2265 monitors the flow on FE’s Star-Juniper 345 kV line for contingent loss of the Hanna-Juniper 345 Line
  normally the LODF for this flowgate is 0.361
  flowgate has a limit of 1080 MW
  at 15:05 EDT the flow as 517 MW on Star-Juniper, 1004 MW on Hanna-Juniper, giving a flowgate value of 520+0.361*1007=884 (82%)
  Chamberlin-Harding 345 opened at 15:05; FE and MISO all missed seeing this
Information on PJM’s current flowgates is available at www.pjm.com/markets-and-operations/etools/oasis/atc-information
22

## Slide 24: The Bad LODF that Maybe Blacked Out the Northeast
At 15:06 EDT (after loss of Chamberlin-Harding 345) #2265 has an incorrect value because its LODF was not automatically updated.
  Value should be 633+0.463*1174=1176 (109%)
  Value was 633 + 0.361*1174=1057 (98%)
At 15:32 the flowgate’s contingent line opened, causing the flowgate to again show the correct value, about 107%
23

## Slide 25: Flows at 15:33 EDT
24

## Slide 26: Estimated Northeast Ohio 138 kV Voltage Contour: 15:33 EDT
25

## Slide 27: IT Issues
MISO RCs had gotten many hundreds of “alarms”
Contingency analysis results were giving pages of violations.
SE would fail because of severe system stress
Inadequate procedures for dealing with SE failure.
FE control center would get “many phone calls;” information was not effectively shared.
26

## Slide 28: Estimated Flows in Northeast Ohio at 15:46 EDT on August 14th 2003
27

## Slide 29: Estimated Northeast Ohio 138 kV Voltage Contour: 15:46 EDT
28

## Slide 30: What Could Have Been Done? Sammis-Star Flow Sensitivities
DOE/NERC
report said
about
1500 MW
of load
shed would have been
needed
29

## Slide 31: Estimated Flows in Northeast Ohio at 16:05 EDT on August 14th 2003
30

## Slide 32: Estimated Northeast Ohio 138 kV Voltage Contour: 16:05 EDT
31

## Slide 33: Path to Cleveland Blocked after Loss of Sammis-Star 16:05:57
Remaining
Paths
Image Source: August 14 2003 Blackout Final Report
32

## Slide 34: 345 kV Lines Trip Across Ohio to West at 16:09
ONTARIO
33

## Slide 35: Generation Trips 16:09:08 – 16:10:27
ONTARIO
Image Source: August 14 2003 Blackout Final Report
34

## Slide 36: Parts of Ohio/Michigan Served Only from Ontario after 16:10:37
Image Source: August 14 2003 Blackout Final Report
35

## Slide 37: Major Power Reversal: 16:10:38
Image Source: August 14 2003 Blackout Final Report
36

## Slide 38: Ontario/Michigan Interface Flows and Voltage
Image Source: August 14 2003 Blackout Final Report
37

## Slide 39: Ties from PJM to New York Open: 16:10:44 (North Ohio Black)
Image Source: August 14 2003 Blackout Final Report
38

## Slide 40: System Islands Break Up and Collapse: 16:10-16:13
Areas Affected by the Blackout
Service maintained
in some area
Some Local Load Interrupted
Image Source: August 14 2003 Blackout Final Report
39

## Slide 41: Are DC LODFs Accurate? August 14th Crash Test
Here are some results from August 14th
Time | Contingency | Element | LODF | DMW (pred) | DMW (act)
15:05 | Chamberlin-Harding 345 | Hanna-Juniper 345 | 0.362 | 179 | 176
15:32 | Hanna-Juniper 345 | Star-Juniper 345 | 0.465 | 545 | 527
15:46 | CantonCentral-Cloverdale 138 | Sammis-Star 345 | 0.164 | 48 | 54
15:46 | same | Cloverdale-Star 138 | 0.234 | 68 | 64
16:06 | Sammis-Star 345 Star-Urban 138 W.Canton-Dale 138 | Star-Juniper 345 | numerous | 517 | 676
16:06 | same | Ashtabula-Perry 345 | numerous | 319 | 408
40
The results are actually quite good, especially considering the extreme system contingencies