## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 19: EMSs, Synthetic Grids, Voltage Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Starting reading Chapter 8
Homework 6 is now due on Thursday Nov 17 but it counts as two regular homeworks.
1

## Slide 3: Grid Equivalent Examples
A 2016 EI case had about 350 lines with a circuit ID of ’99’ and about 60 with ‘EQ’ (out of a total of 102,000)
  Both WECC and the EI use ’99’ or ‘EQ’ circuit IDs to indicate equivalent lines
  One would expect few equivalent lines in interconnect wide models
A 12 year old EI case had about 1633 lines with a circuit ID of ’99’ and 400 with ‘EQ’ (out of a total of 65673)
A 12 year old case with about 5000 buses and 5000 lines had 600 equivalent lines
2

## Slide 4: Energy Management Systems (EMSs)
EMSs are now used to control most large scale electric grids
EMSs developed in the 1970’s and 1980’s out of SCADA systems
  An EMS usually includes a SCADA system; sometimes called a SCADA/EMS
Having a SE is almost the definition of an EMS. The SE then feeds data to the more advanced functions
EMSs have evolved as the industry has evolved, with functionality customized for the application (e.g., a reliability coordinator or a vertically integrated utility)
3

## Slide 5: ERCOT Control Center with EMS
Source: www.texastribune.org/2016/05/17/texas-market-forces-driving-shift-coal-study-says/
4

## Slide 6: ERCOT EMS
Slide source: ERCOT, D. Penney, J. Mandavilli, M. Henry, “Loss of SCADA, EMS or LCC”
5

## Slide 7: ERCOT EMS, cont.
Slide source: ERCOT, D. Penney, J. Mandavilli, M. Henry, “Loss of SCADA, EMS or LCC”
6
In 2021 Anjan Bose and I wrote a white paper for DOE on new research needs in grid operations. This paper also provides a summary of the development of EMSs. The paper is Bose, Anjan, and T. J. Overbye “Electricity Transmission System Research and Development: Grid Operations” In Transmission Innovation Symposium: Modernizing the U.S. Electrical Grid, U.S. Department of Energy 2021 (a link is on my website at overbye.engr.tamu.edu/publications)

## Slide 8: NERC Reliability Coordinators
Source: www.nerc.com/pa/rrm/TLR/Pages/Reliability-Coordinators.aspx
7

## Slide 9: EEI Member Companies
Geographically the map is somewhat sparse because EEI represents investor owned utilities
8

## Slide 10: Electric Coops
9

## Slide 11: Texas Electric Coops
http://www.tecutility.org/about/member-directory
10

## Slide 12: Synthetic Electric Grids
Synthetic electric grids are models of electric grids that were not created to represent any actual electric grid
The below image shows the five bus synthetic grid I used as an undergraduate
Image Source: W.D. Stevenson, Elements of Power Systems, Fourth Edition, McGraw-Hill Book Company New York, 1982 (the first edition was in 1955)

## Slide 13: Geographically-Based Synthetic Electric Grids
Synthetic electric grids can be created with or without reference to actual geography
The image shows an early geographically- based synthetic electric grid
This grid was designed to show concepts to regulators
Image Source: PowerWorld Corporation, 1995

## Slide 14: High-Quality, Geographically-Based Synthetic Electric Grids
High-quality synthetic electric grids are designed to have a wide range of characteristics that are similar to those found in actual electric grids
  “Realistic but not real” to quote Wisconsin colleagues
  Fictional, but hopefully good fiction
  Developed techniques can be applied to real grids
However, importantly these grids are not designed to try to duplicate any actual grid
Over the last five years tremendous progress has been made through ARPA-E at both the transmission and distribution levels

## Slide 15: Current Status: Large-Scale Grids are Now Available
This is an 82,000 bus synthetic model that we publicly released in summer 2018; it is available at electricgrids.engr.tamu.edu
Grid has an
AC power flow solution with n-1 reliability

## Slide 16: The Need for Synthetic Grids
Prior to 9/11/01, a lot of grid information was publically available
Now access to data and models about the actual power grid in the US is quite restricted (e.g., critical energy/electricity infrastructure [CEII])
  What is available is often partial, and can’t be shared
To do effective research, and to drive innovation, researchers need access to common, realistic grid models and data sets
  Scientific principle of reproducibility of results
Synthetic grids and datasets are, of course, designed to augment, not replace actual grids

## Slide 17: The Need for Synthetic Grids, cont.
But the synthetic grids offer some significant advantages, both to industry and researchers
  Since there are no CEII or privacy concerns, full models and their associated datasets can be freely shared; this is particularly helpful for interdisciplinary research
  Synthetic grids can allow future grid scenarios to be considered in-depth (i.e., high renewables or high impact, low frequency events) yet still be potentially public
  Synthetic grids can be customized to represent particular grid idiosyncrasies; utilities can provide this to researchers or potential vendors
    We’ve deliberately designed ours using different voltage levels than those used in the actual grid (e.g., 500/230 versus 345/138 in Texas) to emphasis they are synthetic
  They can be coupled with actual data, like weather
  Synthetic grids can be used for education, including vendor training and short courses

## Slide 18: Our Synthetic Grid Approach
Make grids that look real and familiar by siting them geographically (North America for us) and serving a population density the mimics actual
Goal is to leverage widely available public data
  Geography
  Population density (easily available by post office)
  Load by utility (US FERC 714), state-wide averages
  Existing and planned generation (Form US EIA-860, which contains lots of generator information)
Substation locations and transmission system is entirely fictional (but hopefully good fiction!)

## Slide 19: Synthetic Model Design Process
The assumed peak load is based on population, scaled by geographic values
Much of this is automated, but there is still some manual adjustment
This process can be augmented to couple with detailed distribution grids

## Slide 20: More Details on Design Process
Substation planning: cluster actual population and energy data into correctly-sized substations and assign load, generation, bus voltage levels, and internal branches, along with parameters.
Transmission planning: use iterative penalty-based dc power flow algorithm to place transmission lines, with the Delaunay triangulation and neighborhood as base
Reactive power planning: iterative ac power flow starting from known solution to place capacitors and adjust generator set points.

## Slide 21: Understanding Actual Electric Grid Topology
To make realistic synthetic grids it is important to understand the geographic of actual grids
Actual power grids are geographically consistent
  This is an inherent characteristic that has profound modeling implications
  Examples include line impedance, and constraints such as lakes, rivers, and mountains
Traditionally power system planning models did not include geographic coordinates but this has now changed

## Slide 22: Understanding Actual Electric Grid Topology
Assuming the substation geographic locations are known, the topology of the grid can be discovered, voltage level by voltage level
  Transformers are within substations
At a particular voltage level think of each substation as a node; the minimum spanning tree (MST) is the shortest set of lines to connect all the nodes
The Delaunay triangulation is a triangulation of these points such that no point is inside the circumcircle of any triangle.
The Delaunay triangulation contains the MST

## Slide 23: Use of Delaunay Triangulation
Helps to capture geometric constraints of grids, i.e. substations generally connect to nearby neighbors.
Considering only Delaunay triangulation and 2-3 neighbors cuts potential lines from to , but captures about 98% of actual lines
Transmission Line Category | Average percentage for Eastern Interconnect | Average percentage for Western Interconnect
Min. Span. Tree | 47.8% | 44.3%
Delaunay | 75.6% | 71.1%
2 neighbor | 18.3% | 21.5%
3 neighbor | 4.6% | 5.3%
4 neighbor | 1.1% | 1.4%
5+ neighbor | 0.4% | 0.7%

## Slide 24: Actual Grid Delaunay Triangulation and Minimum Spanning Tree
Below image shows Delaunay triangulation of 42,000 North America substations; statistics only consider single voltage levels; this is computationally fast (order n ln(n))
MST for the EI 500 kV grid black is actual on MST; red is MST without a line; green is other

## Slide 25: Outlier Characteristics are Key
A 76,000 bus North American power flow model has 27,622 transformers with 98 phase shifters
  Impedance correction tables are used for 351, including about 2/3 of the phase shifters; tables can change the impedance by more than two times
The voltage magnitude is controlled at about 19,000 buses (by Gens, LTCs, switched shunts)
  94% regulate their own terminals with about 1100 doing remote regulation. Of this 277 are regulated by three or more devices
Reactive power control interaction is a issue

## Slide 26: Validation: Ensuring High Quality
Based upon data from actual grids we’ve developed a large number of metrics that cover many aspects of both transmission and distribution grids
For example:
  Buses/substation, Voltage levels, Load at each bus
  Generator commitment, dispatch
  Transformer reactance, MVA limit, X/R ratio
  Percent of lines on minimum spanning tree and various neighbors of the Delaunay triangulation
  Bus phase angle differences, flow distribution

## Slide 27: Example Validation Metrics

## Slide 28: Example Validation Metrics, cont.

## Slide 29: Validation Example: Cycle Sizes
Cycles are loops of connected buses. Power systems have many cycles and an important metric to match is to have a similar cycle basis

## Slide 30: Intersections (Transmission Line Crossings)
We’ve found it is important to match properties of electric grids that depend on their physical layout; for example transmission line crossings
  Transmission line right-of-ways are available in EIA datasets; hence line crossings can be analyzed
A paper discussing this is A. Birchfield, T. J. Overbye, “Graph Crossings in Electric Transmission Grids,” 2021 North American Power Symposium, College Station, TX, November 2021. (it is on my website at https://overbye.engr.tamu.edu/publications/)

## Slide 31: Detailed Transmission and Distribution Testing
Full transmission and distribution system studies are being done using a co-simulation framework
  PowerWorld Simulator is used to solve the transmission system and OpenDSS is used to solve each of the distribution circuits
  The simulations are coupled together using the national lab developed HELICS package; one year of simulations took about 3 hours
For Travis County (population 1.2 million) 307,236 meters are served by 488 distribution circuits

## Slide 32: Different Levels of Modeling
Just because we have detailed grids, doesn’t mean we always simulate the coupled transmission and distribution models. Other options are
  Transmission only
  Distribution only
  Full transmission with distribution topology; this can be quite useful for doing multi-infrastructure simulation in which we just need to know what parts of the distribution system are out-of-service

## Slide 33: Synthetic Grid Applications: Innovative Electric Power Education
Lab assignments involving a 2000 bus case have been integrated into Texas A&M’s power classes
Class includes large-system exercises for power flow, economic dispatch, contingency analysis, SCOPF, and transient stability

## Slide 34: Innovative Electric Power Education
One lab challenges students to save the synthetic Texas grid from voltage collapse following a simulated tornado in real-time!
The lab was introduced in Fall 2017; in Fall 2018 it was expanded to be a multi-user simulation. However it did not involve integrated analysis.

## Slide 35: Giving Students (and Others) Experience In Grid Operations
Most electric power students have little or no experience in actually operating an electric grid (real or simulated)
One of our goals is to provide such an experience both in an individually and as part of a team
Developing this involves a combination of the electric grid, the scenario, and the associated simulation environment, and the path to give the users experience with the environment
This also generates data

## Slide 36: The Simulation Environment

## Slide 37: Power System Voltage Stability
Voltage Stability: The ability to maintain system voltage so that both power and voltage are controllable. System voltage responds as expected (i.e., an increase in load causes proportional decrease in voltage).
Voltage Instability: Inability to maintain system voltage. System voltage and/or power become uncontrollable. System voltage does not respond as expected.
Voltage Collapse: Process by which voltage instability leads to unacceptably low voltages in a significant portion of the system; typically results in loss of system load.
36

## Slide 38: Voltage Stability
Two good references are
  P. Kundur, et. al., “Definitions and Classification of Power System Stability,” IEEE Trans. on Power Systems, pp. 1387-1401, August 2004.
  T. Van Cutsem, “Voltage Instability: Phenomena, Countermeasures, and Analysis Methods,” Proc. IEEE, February 2000, pp. 208-227.
Classified by either size of disturbance or duration
  Small or large disturbance: small disturbance is just perturbations about an equilibrium point (power flow)
  Short-term (several seconds) or long-term (many seconds to minutes) (covered in ECEN 667)
37

## Slide 39: Small Disturbance Voltage Stability
Small disturbance voltage stability can be assessed using a power flow (maximum loadability)
Depending on the assumed load model, the power flow can have multiple (or no) solutions
PV curve is created by plotting power versus voltage
Assume Vslack=1.0
Where B is the line susceptance =-10, V is the load voltage
38

## Slide 40: Small Disturbance Voltage Stability
Question: how do the power flow solutions vary as the load is changed?
A Solution: Calculate a series of power flow solutions for various load levels and see how they change
Power flow Jacobian
39

## Slide 41: Maximum Loadability When Power Flow Jacobian is Singular
An important paper considering this was by Sauer and Pai from IEEE Trans. Power Systems in Nov 1990, “Power system steady-state stability and the load-flow Jacobian”
Other earlier papers were looking at the characteristics of multiple power flow solutions
The power flow Jacobian depends on the assumed load model (we’ll see the impact in a few slides)
40

## Slide 42: Relationship Between Stability and Power Flow Jacobian
The Sauer/Pai paper related system stability to the power flow Jacobian by noting that the system dynamics could be written as a set of differential algebraic equations
41

## Slide 43: Relationship Between Stability and Power Flow Jacobian
Then
What Sauer and Pai show is if g/  y is singular then the system is unstable; if g/  y is nonsingular then the system may or may not be stable
Hence it provides an upper bound on stability
42

## Slide 44: Bifurcations
In general, bifurcation is the division of something into two branches or parts
For a dynamic system, a bifurcation occurs when small changes in a parameter cause a new quality of motion of the dynamic system
Two types of bifurcation are considered for voltage stability
  Saddle node bifurcation is the disappearance of an equilibrium point for parameter variation; for voltage stability it is two power flow solutions coalescing with parameter variation
  Hopf bifurcation is cause by two eigenvalues crossing into the right-half plane
43

## Slide 45: PV and QV Curves
PV curves can be traced by plotting the voltage as the real power is increased; QV curves as reactive power is increased
  At least for the upper portion of the curve
Two bus example PV and QV curves
44

## Slide 46: Small Disturbance Voltage Collapse
At constant frequency (e.g., 60 Hz) the complex power transferred down a transmission line is S=VI*
  V is phasor voltage, I is phasor current
  This is the reason for using a high voltage grid
Line real power losses are given by RI2 and reactive power losses by XI2
  R is the line’s resistance, and X its reactance; for a high voltage line X >> R
Increased reactive power tends to drive down the voltage, which increases the current, which further increases the reactive power losses
45