## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 22: Linear Programming, Optimal Power Flow,
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 8
Read the Chapter 3 appendices (3A covers optimization with constraints, 3B covers linear programming, 3D covers dynamic programming, and 3E convex optimization
An excellent book on optimization is Linear and Nonlinear Programming by Luenberger and Ye (the 5th edition came out in 2021)
Homework 6 is due today
Exam 2 is on Thursday Dec 1 during class (for the on campus students); it will be comprehensive, but with more emphasis on the material after the first exam
1

## Slide 3: Quick Coverage of Linear Programming
LP is probably the most widely used mathematical programming technique
It is used to solve linear, constrained minimization (or maximization) problems in which the objective function and the constraints can be written as linear functions
2

## Slide 4: Example Problem 1 (mentioned in Lecture 21)
Assume that you operate a lumber mill which makes both construction-grade and finish-grade boards from the logs it receives. Suppose it takes 2 hours to rough-saw and 3 hours to plane each 1000 board feet of construction-grade boards. Finish-grade boards take 2 hours to rough-saw and 5 hours to plane for each 1000 board feet. Assume that the saw is available 8 hours per day, while the plane is available 15 hours per day. If the profit per 1000 board feet is $100 for construction-grade and $120 for finish-grade, how many board feet of each should you make per day to maximize your profit?
3

## Slide 5: Problem 1 Setup
Notice that all of the equations are linear, but they are inequality, as opposed to equality, constraints; we are seeking to determine the values of x1 and x2
4

## Slide 6: Example Problem 2 (Nutritionist Problem)
A nutritionist is planning a meal with 2 foods: A and B. Each ounce of A costs $ 0.20, and has 2 units of fat, 1 of carbohydrate, and 4 of protein. Each ounce of B costs $0.25, and has 3 units of fat, 3 of carbohydrate, and 3 of protein. Provide the least cost meal which has no more than 20 units of fat, but with at least 12 units of carbohydrates and 24 units of protein.
5

## Slide 7: Problem 2 Setup
Again all of the equations are linear, but they are inequality, as opposed to equality, constraints; we are again seeking to determine the values of x1 and x2; notice there are also more constraints than solution variables
6

## Slide 8: Three Bus Case Formulation
For the earlier three bus system given the initial condition of an overloaded transmission line, minimize the cost of generation such that the change in generation is zero, and the flow on the line between buses 1 and 3 is not violating its limit
Can be setup consider- ing the change in generation, (DPG1, DPG2, DPG3)
7

## Slide 9: Three Bus Case Problem Setup
Line flow constraint
Power balance constraint
8

## Slide 10: LP Standard Form
Maximum problems can be treated as minimizing the negative
The previous examples were not in this form!
9

## Slide 11: Replacing Inequality Constraints with Equality Constraints
The LP standard form does not allow inequality constraints
Inequality constraints can be replaced with equality constraints through the introduction of slack variables, each of which must be greater than or equal to zero
Slack variables have no cost associated with them; they merely tell how far a constraint is from being binding, which will occur when its slack variable is zero
10

## Slide 12: Lumber Mill Example with Slack Variables
Let the slack variables be x3 and x4, so
Minimize the negative
11

## Slide 13: LP Definitions
AB is called the basis matrix
This is a key LP concept!
12

## Slide 14: Fundamental LP Theorem
Given an LP in standard form with A of rank m then
  If there is a feasible solution, there is a basic feasible solution
  If there is an optimal, feasible solution, then there is an optimal, basic feasible solution
Note, there could be a LARGE number of basic, feasible solutions
  Simplex algorithm determines the optimal, basic feasible solution usually very quickly
13

## Slide 15: LP Graphical Interpretation
The LP constraints define a polyhedron in the solution space
  This is a polytope if the polyhedron is bounded and nonempty
  The basic, feasible solutions are vertices of this polyhedron
  With the linear cost function the solution will be at one of vertices
Image: Figure 3.26 from course text
A polyhedron can be unbounded
14

## Slide 16: Simplex Algorithm
The key is to move intelligently from one basic feasible solution (i.e., a vertex) to another, with the goal of continually decreasing the cost function
The algorithm does this by determining the “best” variable to bring into the basis; this requires that another variable exit the basis, while always retaining a basic, feasible solution
This is called pivoting
15

## Slide 17: Determination of Variable to Enter the Basis
To determine which non-basic variable should enter the basis (i.e., one which currently 0), look at how the cost function changes w.r.t. to a change in a non-basic variable (i.e., one that is currently zero)
Elements of xn are all zero, but we are looking to change one to decrease the cost
16

## Slide 18: Determination of Variable to Enter the Basis, cont.
Define the reduced (or relative) cost coefficients as
Elements of this vector tell how the cost function will change for a change in a currently non-basic variable
The variable to enter the basis is usually the one with the most negative relative cost
If all the relative costs are nonnegative then we are at an optimal solution
r is an n-m dimensional row vector
17

## Slide 19: Determination of Variable to Exit Basis
The new variable entering the basis, say a position j, causes the values of all the other basic variables to change. In order to retain a basic, feasible solution, we need to insure no basic variables become negative. The change in the basic variables is given by
18

## Slide 20: Determination of Variable to Exit Basis, cont.
19

## Slide 21: Canonical Form
The Simplex Method works by having the problem in what is known as canonical form
Canonical form is defined as having the m basic variables with the property that each appears in only one equation, its coefficient in that equation is unity, and none of the other basic variables appear in the same equation
Sometime canonical form is readily apparent
Note that with x3 and x4 as basic variables AB is the identity matrix
20

## Slide 22: Canonical Form
Other times canonical form is achieved by initially adding artificial variables to get an initial solution
Example of the nutrition problem in canonical form with slack and artificial variables (denoted as y) used to get an initial basic feasible solution
Note that with y1, y2, and y3 as basic variables AB is the identity matrix
21

## Slide 23: LP Tableau
With the system in canonical form, the Simplex solution process can be illustrated by forming what is known as the LP tableau
  Initially this corresponds to the A matrix, with a column appended to include the b vector, and a row added to give the relative cost coefficients; the last element is the negative of the cost function value
  Define the tableau as Y, with elements Yij
  In canonical form the last column of the tableau gives the values of the basic variables
During the solution the tableau is updated by pivoting
22

## Slide 24: LP Tableau for the Nutrition Problem with Artificial Variables
When in canonical form the relative costs vector is
The initial tableau for the artificial problem is then
Note the last column gives the values of the basic variables
23

## Slide 25: LP Tableau Pivoting
Pivoting is used to move from one basic feasible solution to another
  Select the pivot column (i.e., the variable coming into the basis, say q) as the one with the most negative relative cost
  Select the pivot row (i.e., the variable going out of the basis) as the one with the smallest ratio of xi/Yiq for Yiq >0; define this as row p (xi is given in the last column)
24

## Slide 26: LP Tableau Pivoting for Nutrition Problem
Starting at
Pivot on column q=2; for row get minimum of {20/3, 12/3, 24/3), which is row p=2
25

## Slide 27: LP Tableau Pivoting
Pivoting on element Ypq is done by
  First dividing row p by Ypq to change the pivot element to unity.
  Then subtracting from the kth row Ykq/Ypq times the pth row for all rows with Ykq <> 0
I’m only showing fractions with two ROD digits
26

## Slide 28: LP Tableau Pivoting, Example, cont.
Next pivot on column 1, row 3
Which gives
27

## Slide 29: LP Tableau Pivoting, Example, cont.
Next pivot on column 3, row 1
Which gives
Since there are no
negative relative costs we are done (with getting a starting solution)
28

## Slide 30: LP Tableau Full Problem
The tableau from the end of the artificial problem is used as the starting point for the actual solution
  Remove the artificial variables
  Update the relative costs with the costs from the original problem and update the bottom right-hand corner value
Since none of the relative costs are negative we are done with x1=4, x2=2.7 and x3=4
29

## Slide 31: Marginal Costs of Constraint Enforcement in LP
The marginal costs will be used to determine the OPF locational marginal costs (LMPs)
30

## Slide 32: Nutrition Problem Marginal Costs
In this problem we had basic variables 1, 2, 3; nonbasic variables of 4 and 5
There is no marginal cost with the first constraint since it is not binding; values tell how cost changes if the b values were changed
31

## Slide 33: Lumber Mill Example Solution
Economic interpretation of l is the profit is increased by 35 for every hour we up the first constraint (the saw) and by 10 for every hour we up the second constraint (plane)
32

## Slide 34: Complications
Often variables are not limited to being  0
  Variables with just a single limit can be handled by substitution; for example if x  5 then x-5=z  0
  Bounded variables, high  x  0 can be handled with a slack variable so x + y = high, and x,y  0
Unbounded conditions need to be detected (i.e., unable to pivot); also the solution set could be null
33

## Slide 35: Complications
Degenerate Solutions
  Occur when there are less than m basic variables > 0
  When this occurs the variable entering the basis could also have a value of zero; it is possible to cycle, anti-cycling techniques could be used
Nonlinear cost functions
  Nonlinear cost functions could be approximated by assuming a piecewise linear cost function
Integer variables
  Sometimes some variables must be integers; known as integer programming; we’ll discuss after some power examples
34

## Slide 36: LP Optimal Power Flow
LP OPF was introduced in
  B. Stott, E. Hobson, “Power System Security Control Calculations using Linear Programming,” (Parts 1 and 2) IEEE Trans. Power App and Syst., Sept/Oct 1978
  O. Alsac, J. Bright, M. Prais, B. Stott, “Further Developments in LP-based Optimal Power Flow,” IEEE Trans. Power Systems, August 1990
It is a widely used technique, particularly for real power optimization; it is the technique used in PowerWorld
35

## Slide 37: LP Optimal Power Flow
Idea is to iterate between solving the power flow, and solving an LP with just a selected number of constraints enforced
The power flow (which could be ac or dc) enforces the standard power flow constraints
The LP equality constraints include enforcing area interchange, while the inequality constraints include enforcing line limits; controls include changes in generator outputs
LP results are transferred to the power flow, which is then resolved
36

## Slide 38: LP OPF Introductory Example
In PowerWorld load the B3LP case and then display the LP OPF Dialog (select Add-Ons, OPF Case Info, OPF Options and Results)
Use Solve LP OPF to solve the OPF, initially with no line limits enforced; this is similar to economic dispatch with a single power balance equality constraint
The LP results are available from various pages on the dialog
37

## Slide 39: LP OPF Introductory Example, cont
38

## Slide 40: LP OPF Introductory Example, cont
On use Options, Constraint Options to enable the enforcement of the Line/Transformer MVA limits
39

## Slide 41: LP OPF Introductory Example, cont.
40

## Slide 42: Example 6_23 Optimal Power Flow
Open the case Example6_23_OPF. In this example the load is gradually increased
On the Options, Environment page the simulation can be set to solve an OPF when simulating
41

## Slide 43: Locational Marginal Costs (LMPs)
In an OPF solution, the bus LMPs tell the marginal cost of supplying electricity to that bus
The term “congestion” is used to indicate when there are elements (such as transmission lines or transformers) that are at their limits; that is, the constraint is binding
Without losses and without congestion, all the LMPs would be the same
Congestion or losses causes unequal LMPs
LMPs are often shown using color contours; a challenge is to select the right color range!
42

## Slide 44: Example 6_23 Optimal Power Flow with Load Scale = 1.72
43

## Slide 45: Example 6_23 Optimal Power Flow with Load Scale = 1.72
LP Sensitivity Matrix (A Matrix)
The first row is the power balance constraint, while the second row is the line flow constraint. The matrix only has the line flows that are being enforced.
44

## Slide 46: Example 6_23 Optimal Power Flow with Load Scale = 1.82
This situation is infeasible, at least with available controls. There is a solution because the OPF is allowing one of the constraints to violate (at high cost)
45

## Slide 47: Generator Cost Curve Modeling
LP algorithms require linear cost curves, with piecewise linear curves used to approximate a nonlinear cost function
Two common ways of entering cost information are
  Quadratic function
  Piecewise linear curve
The PowerWorld OPF supports both types
46

## Slide 48: Security Constrained OPF
Security constrained optimal power flow (SCOPF) is similar to OPF except it also includes contingency constraints
  Again the goal is to minimize some objective function, usually the current system cost, subject to a variety of equality and inequality constraints
  This adds significantly more computation, but is required to simulate how the system is actually operated (with N-1 reliability)
A common solution is to alternate between solving a power flow and contingency analysis, and an LP
47

## Slide 49: Security Constrained OPF, cont.
With the inclusion of contingencies, there needs to be a distinction between what control actions must be done pre-contingent, and which ones can be done post-contingent
  The advantage of post-contingent control actions is they would only need to be done in the unlikely event the contingency actually occurs
Pre-contingent control actions are usually done for line overloads, while post-contingent control actions are done for most reactive power control and generator outage re-dispatch
48

## Slide 50: SCOPF Example
We’ll again consider Example 6_23, except now it has been enhanced to include contingencies and we’ve also greatly increased the capacity on the line between buses 4 and 5; named Bus5_SCOPF_DC
Original with line 4-5 limit of 60 MW with 2-5 out
Modified with line 4-5 limit of 200 MVA with 2-5 out
49

## Slide 51: PowerWorld SCOPF Application
Just click the button to solve
Number of times to redo contingency analysis
50

## Slide 52: LP OPF and SCOPF Issues
The LP approach is widely used for the OPF and SCOPF, particularly when implementing a dc power flow approach
A key issue is determining the number of binding constraints to enforce in the LP tableau
  Enforcing too many is time-consuming, enforcing too few results in excessive iterations
The LP approach is limited by the degree of linearity in the power system
  Real power constraints are fairly linear, reactive power constraints much less so
51