## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 6: Power Flow
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 6 from the book
Homework 1 is due Today
Homework 2 is due on Thursday September 22
  Requires the commercial version of PowerWorld with details sent in an email
The ECEN EPG dinner is Saturday October 1st at 5:00 pm at Prof. Davis’s house. The address is 3810 Park Meadow Lane, Bryan, TX 77802.
  RSVP at https://forms.gle/6aye2butgCLDv6bz5 by Sunday, September 25th.
Notation notes: IEEE has a style manual at
  journals.ieeeauthorcenter.ieee.org/wp-content/uploads/sites/7/IEEE-Editorial-Style-Manual-for-Authors.pdf
  Four digit numbers have no comma; ac and dc are lower case (though upper case abbreviations are common)

## Slide 3: Three Bus PowerWorld Simulator Case
Load with
green
arrows
indicating
amount
of MW
flow
Used
to control
output of
generator
Note the
power
balance at
each bus
Direction of green arrow is used to indicate
direction of real power (MW) flow; the blue arrows show the reactive power
PowerWorld Case Name: B3Slow

## Slide 4: Basic Power Control
Opening a circuit breaker causes the power flow to quickly change.
No other way to directly control power flow in a transmission line.
By changing generation we can indirectly change this flow.
Power flow in transmission line is limited by heating considerations
Losses (I^2 R) can heat up the line, causing it to sag.
The change isn’t really instantaneous because of propagation delays, which are near the speed of light; there also wave reflection issues
  This is covered in ECEN 616 and 667
Red is the vs end, green the v2 end

## Slide 5: Transmission Line Limits
Power flow in transmission line is limited by heating considerations.
Losses (I2 R) can heat up the line, causing it to sag.
Each line has a limit; many utilities use winter/summer limits.

## Slide 6: Interconnected Operation Balancing Authority (BA) Areas
North American Eastern and Western grids are divided into balancing authority areas (BA)
  Often just called an area
Transmission lines that join two areas are known as tie-lines.
The net power out of an area is the sum of the flow on its tie-lines.
The flow out of an area is equal to total gen - total load - total losses = tie-flow
Source: www.wecc.org/epubs/StateOfTheInterconnection/Pages/The-Bulk-Power-System.aspx

## Slide 7: RC West Balancing Authorities
Source: www.caiso.com/Documents/RCWestEntities.pdf

## Slide 8: Area Control Error (ACE)
The area control error is the difference between the actual flow out of an area, and the scheduled flow
  ACE also includes a frequency component that we will probably consider later in the semester
Ideally the ACE should always be zero
Because the load is constantly changing, each utility (or ISO) must constantly change its generation to “chase” the ACE
ACE was originally computed by utilities; increasingly it is computed by larger organizations such as ISOs

## Slide 9: PJM Area Control Error: Sept 9, 2022
Source: dataviewer.pjm.com/dataviewer/pages/public/ace.jsf

## Slide 10: Automatic Generation Control
Most utilities (ISOs) use automatic generation control (AGC) to automatically change their generation to keep their ACE close to zero.
Usually the control center calculates ACE based upon tie-line flows; then the AGC module sends control signals out to the generators every couple seconds.

## Slide 11: Three Bus Case on AGC
Net tie flow is
close to zero
Generation
is automatically
changed to match
change in load

## Slide 12: Generator Costs
There are many fixed and variable costs associated with power system operation
The major variable cost is associated with generation.
Cost to generate a MWh can vary widely
For some types of units (such as hydro and nuclear) it is difficult to quantify
More others such as wind and solar the marginal cost of energy is essentially zero (actually negative for wind!)
For thermal units it is straightforward to determine
Many markets have moved from cost-based to price-based generator costs

## Slide 13: Economic Dispatch
Economic dispatch (ED) determines the least cost dispatch of generation for an area.
For a lossless system, the ED occurs when all the generators have equal marginal costs. IC1(PG,1) = IC2(PG,2) = … = ICm(PG,m)

## Slide 14: Power Transactions
Power transactions are contracts between areas to transfer power
Contracts can be for any amount of time at any price for any amount of power
Scheduled power transactions are implemented by modifying the area ACE: ACE = Pactual,tie-flow - Psched

## Slide 15: 100 MW Transaction
Scheduled 100 MW transaction from the Home Area to the Other Area
Net tie-line
flow is now
100 MW

## Slide 16: Security Constrained ED
Transmission constraints often limit system economic operation.
Such limits required a constrained dispatch in order to maintain system security.
In the three bus case the generation at bus 3 must be constrained to avoid overloading the line from bus 2 to bus 3.

## Slide 17: Security Constrained Dispatch
Dispatch is no longer optimal due to need to keep the line
from bus 2 to bus 3 from overloading

## Slide 18: Multi-Area Operation
If areas have direct interconnections then they may directly transact, up to the capacity of their tie-lines.
Actual power flows through the entire network according to the impedance of the transmission lines.
Flow through other areas is known as “parallel path” or “loop flow.”

## Slide 19: Seven Bus Case: One-line
System has three areas
Area Left
has one
bus
Area Right has one bus
Area Top
has five
buses
PowerWorld Case: B7Flat

## Slide 20: Seven Bus Case: Area View
System has
40 MW of
“Loop Flow”
Actual
flow
between
areas
Scheduled
flow

## Slide 21: Seven Bus - Loop Flow?
100 MW Transaction
between Left and Right
Transaction has actually decreased
the loop flow
Note that
Top’s
losses have
increased
from
7.1 MW to
9.6 MW

## Slide 22: Pricing Electricity
Cost to supply electricity to bus is called the locational marginal price (LMP)
Presently some electric markets post LMPs on the web
In an ideal electricity market with no transmission limitations the LMPs are equal
Transmission constraints can segment a market, resulting in differing LMP
Determination of LMPs requires the solution on an Optimal Power Flow (OPF), which will be covered later in the semester

## Slide 23: Three Bus LMPs – Constraints Ignored
Line from Bus 1 to Bus 3 is over-loaded; all buses have same marginal cost
Gen 1’s
cost
is $10
per
MWh
Gen 2’s
cost
is $12
per
MWh
PowerWorld Case: B3LP

## Slide 24: Three Bus LMPs – Constraint Unforced
Line from 1 to 3 is no longer overloaded, but now
the marginal cost of electricity at bus 3 is $14 / MWh

## Slide 25: Example Real Grid LMPs
Every few minutes LMPs are posted online for several different independent system operators
Image2 Source: https://www.misoenergy.org/markets-and-operations/real-time--market-data/real-time-displays/
Image1 Source: http://www.ercot.com/content/cdr/contours/rtmLmp.html
MISO’s from 6/13/2022

## Slide 26: Sometimes There is Not Much LMP Variation
Image Source: http://www.ercot.com/content/cdr/contours/rtmLmp.html
ERCOT from 9/10/2022

## Slide 27: Advanced Power Flow
Next slides cover some more advanced power flow topics that need to be considered in many commercial power flow studies
An important consideration in the power flow is the assumed time scale of the response, and the assumed model of operator actions
  Planning power flow studies usually assume automatic modeling of operator actions and a longer time frame of response (controls have time to reach steady-state)
    For example, who is actually doing the volt/var control
  In real-time applications operator actions are usually not automated and controls may be more limited in time

## Slide 28: Quasi-Newton Power Flow Methods
First we consider some modified versions of the Newton power flow (NPF)
Since most of the computation in the NPF is associated with building and factoring the Jacobian matrix, J, the focus is on trying to reduce this computation
In a pure NPF J is build and factored each iteration
Over the years pretty much every variation of the NPF has been tried; here we just touch on the most common
Whether a method is effective can be application dependent
  For example, in contingency analysis we are usually just resolving a solved case with an often small perturbation

## Slide 29: Quasi-Newton Power Flow Methods
The simplest modification of the NPF results when J is kept constant for a number of iterations, say k iterations
  Sometimes known as the Dishonest Newton
The approach balances increased speed per iteration, with potentially more iterations to perform
There is also an increased possibility for divergence
Since the mismatch equations are not modified, if it converges it should converge to the same solution as the NPF
These methods are not commonly used, except in very short duration, sequential power flows with small mismatches

## Slide 30: Dishonest N-R Example
We pay a price
in increased
iterations, but
with decreased
computation
per iteration; that price is too high in this example
29

## Slide 31: Decoupled Power Flow
Rather than not updating the Jacobian, the decoupled power flow takes advantage of characteristics of the power grid in order to decouple the real and reactive power balance equations
  There is a strong coupling between real power and voltage angle, and reactive power and voltage magnitude
  There is a much weaker coupling between real power and voltage magnitude, and reactive power and voltage angle
Key reference is B. Stott, “Decoupled Newton Load Flow,” IEEE Trans. Power. App and Syst., Sept/Oct. 1972, pp. 1955-1959

## Slide 32: Decoupled Power Flow Formulation