## Slide 1: ECEN 615 Methods of Electric Power Systems Analysis
Lecture 7: Advanced Power Flow, Gaussian Elimination, Sparse Systems
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 6 from the book
  The book presents the power flow using the polar form for the Ybus elements
Homework 2 is due on Thursday September 22
The ECEN EPG dinner is Saturday October 1st at 5:00 pm at Prof. Davis’s house. The address is 3810 Park Meadow Lane, Bryan, TX 77802.
  RSVP at https://forms.gle/6aye2butgCLDv6bz5 by Sunday, September 25th.

## Slide 3: Larger Sized Grid Power Flow Example
Demonstration of some issues with solving power flows on larger cases
  Example is done using the 2000 bus synthetic grid from Homework 2

## Slide 4: Decoupled Power Flow
Rather than not updating the Jacobian, the decoupled power flow takes advantage of characteristics of the power grid in order to decouple the real and reactive power balance equations
  There is a strong coupling between real power and voltage angle, and reactive power and voltage magnitude
  There is a much weaker coupling between real power and voltage magnitude, and reactive power and voltage angle
Key reference is B. Stott, “Decoupled Newton Load Flow,” IEEE Trans. Power. App and Syst., Sept/Oct. 1972, pp. 1955-1959

## Slide 5: Decoupled Power Flow Formulation

## Slide 6: Decoupling Approximation
5

## Slide 7: Off-diagonal Jacobian Terms
By assuming ½ the elements are zero, we only have to do ½ the computations

## Slide 8: Decoupled N-R Region of Convergence
The high solution ROC is actually larger than with the standard NPF. Obviously this is no a good a way to get the low solution

## Slide 9: Fast Decoupled Power Flow, cont.
By continuing with Jacobian approximations we can obtain a reasonable approximation that is independent of the voltage magnitudes/angles.
  This means the Jacobian need only be built/inverted once per power flow solution
This approach is known as the fast decoupled power flow (FDPF)
FDPF uses the same mismatch equations as standard power flow (just scaled) so it should have same solution
The FDPF is widely used, though usually only for an approximate solution
  Key fast decoupled power flow reference is B. Stott, O. Alsac, “Fast Decoupled Load Flow,” IEEE Trans. Power App. and Syst., May 1974, pp. 859-869
  Modified versions also exist, such as D. Jajicic and A. Bose, “A Modification to the Fast Decoupled Power Flow for Networks with High R/X Ratios, “IEEE Transactions on Power Sys., May 1988, pp. 743-746

## Slide 10: FDPF Approximations
To see the impact on the real power equations recall

## Slide 11: FDPF Approximations
With the approximations for the diagonal term we get
Hence the Jacobian for the real equations can be approximated as –B

## Slide 12: FPDF Approximations
For the reactive power equations we also scale by Vi
For the Jacobian off-diagonals we get

## Slide 13: FDPF Approximations
And for the reactive power Jacobian diagonal we get
As derived the real and reactive equations have a constant Jacobian equal to –B
  Usually modifications are made to omit from the real power matrix elements that affect reactive flow (like shunts) and from the reactive power matrix elements that affect real power flow, like phase shifters
  We’ll call the real power matrix B’ and the reactive B”

## Slide 14: FDPF Region of Convergence

## Slide 15: FDPF Cautions
The FDPF works well as long as the previous approximations hold for the entire system
With the movement towards modeling larger systems, with more of the lower voltage portions of the system represented (for which r/x ratios are higher) it is quite common for the FDPF to get stuck because small portions of the system are ill-behaved
The FDPF is commonly used to provide an initial guess of the solution for contingency analysis

## Slide 16: DC Power Flow
The “DC” power flow makes the most severe approximations:
  completely ignore reactive power, assume all the voltages are always 1.0 per unit, ignore line conductance
This makes the power flow a linear set of equations, which can be solved directly
The term dc power flow actually dates from the time of the old network analyzers (going back into the 1930’s)
Not to be confused with the inclusion of HVDC lines in the standard NPF
P sign convention is generation is positive

## Slide 17: DC Power Flow References
I don’t think a classic dc power flow paper exists; a nice formulation is given in our book Power Generation and Control book by Wood, Wollenberg and Sheble
The August 2009 paper in IEEE Transactions on Power Systems, “DC Power Flow Revisited” (by Stott, Jardim and Alsac) provides good coverage
T. J. Overbye, X. Cheng, and Y. Sun, “A comparison of the AC and DC power flow models for LMP Calculations,” in Proc. 37th Hawaii Int. Conf. System Sciences, 2004, compares the accuracy of the approach

## Slide 18: DC Power Flow Example
Example from Power System Analysis and Design, by Glover, Overbye, Sarma, 6th Edition

## Slide 19: DC Power Flow in PowerWorld
PowerWorld allows for easy switching between the dc and ac power flows (case Aggieland37)
To use the dc approach in PowerWorld select Tools, Solve, DC Power Flow
Notice there are no losses

## Slide 20: Linear System Solution: Introduction
A problem that occurs in many is fields is the solution of linear systems Ax = b where A is an n by n matrix with elements aij, and x and b are n-vectors with elements xi and bi respectively
In power systems we are particularly interested in systems when n is relatively large and A is sparse
  How large is large is changing
A matrix is sparse if a large percentage of its elements have zero values
Goal is to understand the computational issues (including complexity) associated with the solution of these systems

## Slide 21: Introduction, cont.
Sparse matrices arise in many areas, and can have domain specific structures
  Symmetric matrices
  Structurally symmetric matrices
  Tridiagnonal matrices
  Banded matrices
A good (and free) book on sparse matrices is available at www-users.cs.umn.edu/~saad/IterMethBook_2ndEd.pdf
ECEN 615 is focused on problems in the electric power domain; it is not a general sparse matrix course
  Much of the early sparse matrix work was done in power!

## Slide 22: Gaussian Elimination
The best known and most widely used method for solving linear systems of algebraic equations is attributed to Gauss
Gaussian elimination avoids having to explicitly determine the inverse of A, which is O(n3)
Gaussian elimination can be readily applied to sparse matrices
Gaussian elimination leverages the fact that scaling a linear equation does not change its solution, nor does adding on linear equation to another

## Slide 23: Gaussian Elimination, cont.
Gaussian elimination is the elementary procedure in which we use the first equation to eliminate the first variable from the last n-1 equations, then we use the new second equation to eliminate the second variable from the last n-2 equations, and so on
After performing n-1 such eliminations we end up with a triangular system which is easily solved in a backward direction

## Slide 24: Example 1
We need to solve for x in the system
The three elimination steps are given on the next slides; for simplicity, we have appended the r.h.s. vector to the matrix
First step is set the diagonal element of row 1 to 1 (i.e., normalize it)

## Slide 25: Example 1, cont.
Eliminate x1 by subtracting row 1 from all the rows below it

## Slide 26: Example 1, cont.
Eliminate x2 by subtracting row 2 from all the rows below it

## Slide 27: Example 1, cont.
Elimination of x3 from row 3 and 4

## Slide 28: Example 1, cont.
Then, we solve for x by “going backwards”, i.e., using back substitution:

## Slide 29: LU Decomposition
What we did with Gaussian elimination can be thought of as changing the form of the matrix to create two matrices with special structure
One matrix, shown on the last slide, is upper triangular
The second matrix, a lower triangular one, keeps track of the operations we did to get the upper triangular matrix
These concepts will be helpful for a computer implementation of the algorithm and for its application to sparse systems

## Slide 30: LU Decomposition Theorem
Any nonsingular matrix A has the following factorization:
where U could be the upper triangular matrix previously developed (with 1’s on its diagonals) and L is a lower triangular matrix defined by

## Slide 31: LU Decomposition Application
As a result of this theorem we can rewrite
Can also be set so U has non unity diagonals
Once A has been factored, we can solve for x by first solving for y, a process known as forward substitution, then solving for x in a process known as back substitution
In the previous example we can think of L as a record of the forward operations preformed on b.

## Slide 32: LDU Decomposition
In the previous case we required that the diagonals of U be unity, while there was no such restriction on the diagonals of L
An alternative decomposition is
where D is a diagonal matrix, and the lower triangular matrix is modified to require unity for the diagonals (we’ll just use the LU approach in 615)

## Slide 33: Symmetric Matrix Factorization
The LDU formulation is quite useful for the case of a symmetric matrix
Hence only the upper triangular elements and the diagonal elements need to be stored, reducing storage by almost a factor of 2

## Slide 34: Symmetric Matrix Factorization
There are also some computational benefits from factoring symmetric matrices. However, since symmetric matrices are not common in power applications, we will not consider them in-depth
However, topologically symmetric sparse matrices are quite common, so those will be our main focus

## Slide 35: Pivoting
An immediate problem that can occur with Gaussian elimination is the issue of zeros on the diagonal; for example
This problem can be solved by a process known as “pivoting,” which involves the interchange of either both rows and columns (full pivoting) or just the rows (partial pivoting)
  Partial pivoting is much easier to implement, and actually can be shown to work quite well

## Slide 36: Pivoting, cont.
In the previous example the (partial) pivot would just be to interchange the two rows obviously we need to keep track of the interchanged rows!
Partial pivoting can be helpful in improving numerical stability even when the diagonals are not zero
  When factoring row k interchange rows so the new diagonal is the largest element in column k for rows j >= k

## Slide 37: LU Algorithm Without Pivoting Processing by row
We will use the more common approach of having ones on the diagonals of L. Also in the common, diagonally dominant power system problems pivoting is not needed. The below algorithm is in row form (useful with sparsity!)
For i := 2 to n Do Begin // This is the row being processed
For j := 1 to i-1 Do Begin // Rows subtracted from row i
A[i,j] = A[i,j]/A[j,j] // This is the scaling
For k := j+1 to n Do Begin // Go through each column in i
A[i,k] = A[i,k] - A[i,j]*A[j,k]
End;
End;
End;

## Slide 38: LU Example
Starting matrix
First row is unchanged; start with i=2
Result with i=2, j=1; done with row 2
A[2,2]= A[2,2]-A[2,1]*A[1,2]
=12-(-0.25)*(-12) =9
A[2,3] = A[2,3]-A[2,1]*A[1,3]
=-6 –(-0.25)*(-5) = -7.25

## Slide 39: LU Example, cont.
Result with i=3, j=1;
Result with i=3, j=2; done with row 3; done!
A[3,1]= A[3,1]/A[1,1]
=-4/20= -0.2
A[3,2] = A[3,2] – A[3,1]*A[1,2]
A[3,2] = -3 – (-0.2)*(-12) = -5.4
A[3,3] = 8 – (-0.2)*(-5) = 7
A[3,2]= A[3,2]/A[2,2]
=-5.4/9= -0.6
A[3,3] = A[3,3] – A[3,2]*A[2,3]
A[3,3] = 7 – (-0.6)*(-7.25) =2.65

## Slide 40: LU Example, cont.
Original matrix is used to hold L and U
With this approach the original A matrix has been replaced by the factored values!

## Slide 41: Forward Substitution
Forward substitution solves with values in b being over written (replaced by the y values) For i := 2 to n Do Begin // This is the row being processed
For j := 1 to i-1 Do Begin
b[i] = b[i] - A[i,j]*b[j] // This is just using the L matrix
End;
End;

## Slide 42: Forward Substitution Example

## Slide 43: Backward Substitution
Backward substitution solves (with values of y contained in the b vector as a result of the forward substitution)
For i := n to 1 Do Begin // This is the row being processed
For j := i+1 to n Do Begin
b[i] = b[i] - A[i,j]*b[j] // This is just using the U matrix
End;
b[i] = b[i]/A[i,i] // The A[i,i] values are <> 0 if it is nonsingular
End

## Slide 44: Backward Substitution Example