## Slide 1: ECEN 667 Power System Stability
Lecture 10: Exciters
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 4
Homework 3 is due on Thursday Oct 7
Homework 4 is assigned today, but will not need to be turned in (just done before the first exam)
Exam 1 will be on Oct 14 in class
  For the distance learners we usually use Honorlock (though I know for some that won’t work)
  Exams are closed book, closed notes, but you can bring in one 8.5 by 11 inch note sheet and can use calculators

## Slide 3: Dynamic Models in the Physical Structure: Exciters
Machine
Governor
Exciter
Load
Char.
Load
Relay
Line
Relay
Stabilizer
Generator
P, Q
Network
Network control
Loads
Load control
Fuel
Source
Supply control
Furnace and Boiler
Pressure control
Turbine
Speed control
V, I
Torque
Steam
Fuel
Electrical System
Mechanical System
Voltage Control
P. Sauer and M. Pai, Power System Dynamics and Stability, Stipes Publishing, 2006.

## Slide 4: Larger Scale Stability Study
An example of a larger scale stability study we did is available on my website
  overbye.engr.tamu.edu/publications/
  See the first paper in 2022 (from HICSS) or the PSERC report (number 18 in 2021)
The study looked a stability aspects of a synchronous connection of the North American East and WECC grids
The power flow model had 110,000 buses and 13,700 generators; for stability it had 246 different types of dynamic models, 61,000 model instances and more than 200,000 differential equations
We also studied an 82,000 bus synthetic grid

## Slide 5: Larger Scale Stability Study
The below figures are for the 82,000 bus synthetic grid

## Slide 6: Exciter Models

## Slide 7: Exciters, Including AVR
Exciters are used to control the synchronous machine field voltage and current
  Usually modeled with automatic voltage regulator included
A useful reference is IEEE Std 421.5-2016
  Updated from the 2005 edition
  Covers the major types of exciters used in transient stability
  Continuation of standard designs started with "Computer Representation of Excitation Systems," IEEE Trans. Power App. and Syst., vol. pas-87, pp. 1460-1464, June 1968
Another reference is P. Kundur, Power System Stability and Control, EPRI, McGraw-Hill, 1994
  Exciters are covered in Chapter 8 as are block diagram basics

## Slide 8: Functional Block Diagram
Image source: Fig 8.1 of Kundur, Power System Stability and Control

## Slide 9: Potential Types of Exciters
None, which would be the case for a permanent magnet generator
  primarily used with wind turbines with ac-dc-ac converters
DC: Utilize a dc generator as the source of the field voltage through slip rings
AC: Use an ac generator on the generator shaft, with output rectified to produce the dc field voltage; brushless with a rotating rectifier system
Static: Exciter is static, with field current supplied through slip rings

## Slide 10: IEEET1 Exciter
We’ll start with a common exciter model, the IEEET1 based on a dc generator, and develop its structure
  This model was standardized in a 1968 IEEE Committee Paper with Fig 1. from the paper shown below

## Slide 11: Block Diagram Basics
The following slides will make use of block diagrams to explain some of the models used in power system dynamic analysis. The next few slides cover some of the block diagram basics.
To simulate a model represented as a block diagram, the equations need to be represented as a set of first order differential equations
Also the initial state variable and reference values need to be determined

## Slide 12: Integrator Block
Equation for an integrator with u as an input and y as an output is
In steady-state with an initial output of y0, the initial state is y0 and the initial input is zero
u
y

## Slide 13: First Order Lag Block
Equation with u as an input and y as an output is
In steady-state with an initial output of y0, the initial state is y0 and the initial input is y0/K
Commonly used for measurement delay (e.g., TR block with IEEE T1)
u
y
Output of Lag Block
Input

## Slide 14: Derivative Block
Block takes the derivative of the input, with scaling KD and a first order lag with TD
  Physically we can't take the derivative without some lag
  An example is the feedback block in the IEEET1 model
In steady-state the output of the block is zero
State equations require a more general approach
u
y

## Slide 15: State Equations for More Complicated Functions
There is not a unique way of obtaining state equations for more complicated functions with a general form
To be physically realizable we need n >= m

## Slide 16: General Block Diagram Approach
One integration approach is illustrated in the below block diagram
Image source: W.L. Brogan, Modern Control Theory, Prentice Hall, 1991, Figure 3.7

## Slide 17: Derivative Example
Write in form
Hence b0=0, b1=KD/TD, a0=1/TD
Define single state variable x, then
Initial value of x is found by recognizing y is zero so x = -b1u

## Slide 18: Lead-Lag Block
In exciters such as the EXDC1 the lead-lag block is used to model time constants inherent in the exciter; the values are often zero (or equivalently equal)
In steady-state the input is equal to the output
To get equations write in form with b0=1/TB, b1=TA/TB, a0=1/TB
u
y
Output of Lead/Lag
input

## Slide 19: Lead-Lag Block
The equations are with then
b0=1/TB, b1=TA/TB, a0=1/TB
The steady-state requirement that u = y is readily apparent

## Slide 20: Limits: Windup versus Nonwindup
When there is integration, how limits are enforced can have a major impact on simulation results
Two major flavors: windup and non-windup
Windup limit for an integrator block
If Lmin  v  Lmax then y = v
else If v < Lmin then y = Lmin, else if v > Lmax then y = Lmax
u
y
Lmax
Lmin
v
The value of v is NOT limited, so its value can "windup" beyond the limits, delaying backing off of the limit

## Slide 21: Limits on First Order Lag
Windup and non-windup limits are handled in a similar manner for a first order lag
u
y
Lmax
Lmin
v
If Lmin  v  Lmax then y = v
else If v < Lmin then y = Lmin, else if v > Lmax then y = Lmax
Again the value of v is NOT limited, so its value can "windup" beyond the limits, delaying backing off of the limit

## Slide 22: Non-Windup Limit First Order Lag
With a non-windup limit, the value of y is prevented from exceeding its limit
Lmax
Lmin
u
y

## Slide 23: Lead-Lag Non-Windup Limits
There is not a unique way to implement non-windup limits for a lead-lag. This is the one from IEEE 421.5-1995 (Figure E.6)
T2 > T1, T1 > 0, T2 > 0
If y > B, then x = B
If y < A, then x = A
If B y  A, then x = y

## Slide 24: Ignored States
When integrating block diagrams often states are ignored, such as a measurement delay with TR=0
In this case the differential equations just become algebraic constraints
Example: For block at right, as T0, v=Ku
With lead-lag it is quite common for TA=TB, resulting in the block being ignored
u
y
Lmax
Lmin
v

## Slide 25: Brief Review of DC Machines
Prior to widespread use of machine drives, dc motors had a important advantage of easy speed control
On its stator a dc machine has either a permanent magnet or a single concentrated winding
Rotor (armature) currents are supplied through brushes and the commutator
Equations are
The f subscript refers to the field, the a to the armature; w is the machine's speed, G is a constant. In a permanent magnet machine the field flux is constant, the field equation goes away, and the field impact is embedded in a equivalent constant to Gif
Taken mostly from M.A. Pai, Power Circuits and Electromechanics

## Slide 26: Review of DC Machines
The purpose of the next few slides is to provide insight into the source of portions of the block diagrams for various types of exciters

## Slide 27: Types of DC Machines
If there is a field winding (i.e., not a permanent magnet machine) then the machine can be connected in the following ways
  Separately-excited: Field and armature windings are connected to separate power sources
    For an exciter, control is provided by varying the field current (which is stationary), which changes the armature voltage
  Series-excited: Field and armature windings are in series
  Shunt-excited: Field and armature windings are in parallel

## Slide 28: Separately Excited DC Exciter
(to sync
mach)
s1 is coefficient of dispersion, modeling the flux leakage

## Slide 29: Separately Excited DC Exciter
Relate the input voltage, ein1, to vfd
Assuming a constant speed w1
Solve above for ff1 which was used in the previous slide

## Slide 30: Separately Excited DC Exciter
If it was a linear magnetic circuit, then vfd would be proportional to in1; for a real system we need to account for saturation
Without saturation we can write

## Slide 31: Separately Excited DC Exciter
This equation is then scaled based on the synchronous machine base values

## Slide 32: Separately Excited Scaled Values
Thus we have
VR is the scaled output of the voltage regulator amplifier

## Slide 33: The Self-Excited Exciter
When the exciter is self-excited, the amplifier voltage appears in series with the exciter field
Note the additional Efd term on the end

## Slide 34: Self and Separated Excited Exciters
The same model can be used for both by just modifying the value of KE

## Slide 35: Exciter Model IEEET1 KE Values
Example IEEET1 Values from a large system
The KE equal 1 are separately excited, and KE close to zero are self excited

## Slide 36: Saturation
A number of different functions can be used to represent the saturation
The quadratic approach is now quite common
Exponential function could also be used
This is the same function used with the machine models

## Slide 37: Exponential Saturation
In Steady state

## Slide 38: Exponential Saturation Example
Given:
Find:

## Slide 39: Voltage Regulator Model
Amplifier
In steady state
As KA is increased
There is often a droop in regulation
Modeled as a first order differential equation

## Slide 40: Feedback
This control system can often exhibit instabilities, so some type of feedback is used
One approach is a stabilizing transformer
Designed with a large Lt2 so It2  0

## Slide 41: Feedback

## Slide 42: IEEET1 Model Evolution
The original IEEET1, from 1968, evolved into the EXDC1 in 1981
Image Source: Fig 3 of "Excitation System Models for Power Stability Studies," IEEE Trans. Power App. and Syst., vol. PAS-100, pp. 494-509, February 1981
1968
1981
Note, KE in the feedback is the same in both models

## Slide 43: IEEEX1
This is from 1979, and is the EXDC1 with the potential for a measurement delay and inputs for under or over excitation limiters

## Slide 44: IEEET1 Evolution
In 1992 IEEE Std 421.5-1992 slightly modified the EXDC1, calling it the DC1A (modeled as ESDC1A)
Image Source: Fig 3 of IEEE Std 421.5-1992
VUEL is a signal from an under- excitation limiter, which we'll cover later
Same model is in 421.5-2005

## Slide 45: IEEET1 Evolution
Slightly modified in Std 421.5-2016
Note the minimum limit on EFD
There is also the addition to the input of voltages from a stator current limiters (VSCL) or over excitation limiters (VOEL)

## Slide 46: IEEET1 Example
Assume previous GENROU case with saturation. Then add a IEEE T1 exciter with KA=50, TA=0.04, KE=-0.06, TE=0.6, VR,max=1.0, VR,min= -1.0 For saturation assume SE(2.8) = 0.04, SE(3.73)=0.33
Saturation function is 0.1621(EFD-2.303)2 (for EFD > 2.303); otherwise zero
EFD is initially 3.22
SE(3.22)*EFD=0.437
(VR-SE*EFD)/KE=EFD
VR =0.244
VREF = 0.244/Ka +VT =0.0488 +1.0946=1.09948
Case B4_GENROU_Sat_IEEET1

## Slide 47: IEEE T1 Example
For 0.1 second fault (from before), plot of EFD and the terminal voltage is given below
Initial V4=1.0946, final V4=1.0973
  Steady-state error depends on the value of KA

## Slide 48: IEEET1 Example
Same case, except with KA=500 to decrease steady-state error, no VR limits; this case is actually unstable

## Slide 49: IEEET1 Example
With KA=500 and rate feedback, KF=0.05, TF=0.5
Initial V4=1.0946, final V4=1.0957

## Slide 50: WECC Case Type 1 Exciters
In a recent WECC case with 3519 exciters, 20 are modeled with the IEEE T1, 156 with the EXDC1 20 with the ESDC1A (and none with IEEEX1)
Graph shows KE value for the EXDC1 exciters in case; about 1/3 are separately excited, and the rest self excited
  A value of KE equal zero indicates code should set KE so Vr initializes to zero; this is used to mimic the operator action of trimming this value