## Slide 1: ECEN 667 Power System Stability
Lecture 11: Exciters and Governors
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 4
Homework 3 is due today
Homework 4 will not need to be turned in (just done before the first exam)
Exam 1 will be on Oct 14 in class
  For the distance learners we usually use Honorlock (though I know for some that won’t work)
  Exams are closed book, closed notes, but you can bring in one 8.5 by 11 inch note sheet and can use calculators

## Slide 3: Governor Models

## Slide 4: Prime Movers and Governors
Synchronous generator is used to convert mechanical energy from a rotating shaft into electrical energy
The "prime mover" is what converts the orginal energy source into the mechanical energy in the rotating shaft
Possible sources: 1) steam (nuclear, coal, combined cycle, solar thermal), 2) gas turbines, 3) water wheel (hydro turbines), 4) diesel/ gasoline, 5) wind (which we'll cover separately)
The governor is used to control the speed
Image source: http://upload.wikimedia.org/wikipedia/commons/1/1e/Centrifugal_governor.png

## Slide 5: Prime Movers and Governors
In transient stability collectively the prime mover and the governor are called the "governor"
As has been previously discussed, models need to be appropriate for the application
In transient stability the response of the system for seconds to perhaps minutes is considered
Long-term dynamics, such as those of the boiler and automatic generation control (AGC), are usually not considered
These dynamics would need to be considered in longer simulations (e.g. dispatcher training simulator (DTS)

## Slide 6: Power Grid Disturbance Example
Time in Seconds
Figures show the frequency change as a result of the sudden loss of a large amount of generation in the Southern WECC
Frequency Contour
Freq. Hz)

## Slide 7: Frequency Response for Generation Loss
In response to a rapid loss of generation, in the initial seconds the system frequency will decrease as energy stored in the rotating masses is transformed into electric energy
  Some generation, such as solar PV has no inertia, and for most new wind turbines the inertia is not seen by the system
Within seconds governors respond, increasing the power output of controllable generation
  Many conventional units are operated so they only respond to over frequency situations
  Solar PV and wind are usually operated in North America at maximum power so they have no reserves to contribute

## Slide 8: Governor Response: Thermal Versus Hydro
Thermal units respond quickly, hydro ramps slowly (and goes down initially), wind and solar usually do not respond. And many units are set to not respond!
Time in Seconds
Normalized output

## Slide 9: Some Good References
Kundur, Power System Stability and Control, 1994
Wood, Wollenberg and Sheble, Power Generation, Operation and Control, third edition, 2013
IEEE PES, "Dynamic Models for Turbine-Governors in Power System Studies," Jan 2013
"Dynamic Models for Fossil Fueled Steam Units in Power System Studies," IEEE Trans. Power Syst., May 1991, pp. 753-761
"Hydraulic Turbine and Turbine Control Models for System Dynamic Studies," IEEE Trans. Power Syst., Feb 1992, pp. 167-179

## Slide 10: 2600 MW Loss Frequency Recovery
Frequency recovers in about ten minutes

## Slide 11: Frequency Response Definition
FERC defines in RM13-11: “Frequency response is a measure of an Interconnection’s ability to stabilize frequency immediately following the sudden loss of generation or load, and is a critical component of the reliable operation of the Bulk-Power System, particularly during disturbances and recoveries.”
Design Event for WECC is N-2 (Palo Verde Outage) not to result in UFLS (59.5 Hz in WECC)
Source: wecc.biz/Reliability/Frequency%20Response%20Analysis%20-%20Dmitry%20Kosterev.pdf

## Slide 12: Frequency Response Measure
Source: wecc.biz/Reliability/Frequency%20Response%20Analysis%20-%20Dmitry%20Kosterev.pdf

## Slide 13: WECC Interconnection Performance
Source: wecc.biz/Reliability/Frequency%20Response%20Analysis%20-%20Dmitry%20Kosterev.pdf

## Slide 14: Control of Generation Overview
Goal is to maintain constant frequency with changing load
If there is just a single generator, such with an emergency generator or isolated system, then an isochronous governor is used
  Integrates frequency error to insure frequency goes back to the desired value
  Cannot be used with interconnected systems because of "hunting"
Image source: Wood/Wollenberg, 2nd edition

## Slide 15: Generator “Hunting”
Control system “hunting” is oscillation around an equilibrium point
Trying to interconnect multiple isochronous generators will cause hunting because the frequency setpoints of the two generators are never exactly equal
  One will be accumulating a frequency error trying to speed up the system, whereas the other will be trying to slow it down
  The generators will NOT share the power load proportionally

## Slide 16: Isochronous Gen Example
WSCC 9 bus from before, gen 3 dropping (85 MW)
  No infinite bus, gen 1 is modeled with an isochronous generator (PW ISOGov1 model)
Gen 2 is modeled with no governor, so its mechanical power stays fixed
Case is wscc_9bus_IsoGov

## Slide 17: Isochronous Gen Example
Graph shows the change in the mechanical output
All the change in MWs due to the loss of gen 3 is being picked up by gen 1

## Slide 18: Droop Control
To allow power sharing between generators the solution is to use what is known as droop control, in which the desired set point frequency is dependent upon the generator’s output
R is known as the regulation constant or droop; a typical value is 4 or 5%.
At 60 Hz and a 5% droop, each 0.1 Hz change would change the output by 0.1/(60*0.05)=
3.33%

## Slide 19: WSCC 9 Bus Droop Example
Assume the previous gen 3 drop contingency (85 MW), and that gens 1 and 2 have ratings of 500 and 250 MVA respectively and governors with a 5% droop. What is the final frequency (assuming no change in load)?

## Slide 20: WSCC 9 Bus Droop Example
The below graphs compare the mechanical power and generator speed; note the steady-state values match the calculated 59.66 Hz value
Case is wscc_9bus_TGOV1

## Slide 21: Quick Interconnect Calculation
When studying a system with many generators, each with the same (or close) droop, then the final frequency deviation is
The online generator summation should only include generators that actually have governors that can respond, and does not take into account generators hitting their limits
The online generator group obviously does not include the contingency generator(s) that are opened

## Slide 22: Larger System Example
As an example, consider the 37 bus, nine generator example from earlier; assume one generator with 42 MW is opened. The total MVA of the remaining generators is 1132. With R=0.05
Case is Bus37_TGOV1

## Slide 23: WECC Interconnect Frequency Response
Data for the four major interconnects is available from NERC; these are the values between points A and B
Source: www.nerc.com/pa/RAPA/ri/Pages/InterconnectionFrequencyResponse.aspx
A higher value is better (more generation for a 0.1 Hz change)

## Slide 24: Eastern Interconnect Frequency Response
The larger Eastern Interconnect on average has a higher value

## Slide 25: ERCOT Interconnect Frequency Response
Source: www.nerc.com/pa/RAPA/ri/Pages/InterconnectionFrequencyResponse.aspx
An ERCOT a lower value

## Slide 26: Impact of Inertia (H)
Final frequency is determined by the droop of the responding governors
How quickly the frequency drops depends upon the generator inertia values
The least frequency deviation occurs with high inertia and fast governors

## Slide 27: Restoring Frequency to 60 (or 50) Hz
In an interconnected power system the governors to not automatically restore the frequency to 60 Hz
Rather done via the ACE (area control area calculation). Previously we defined ACE as the difference between the actual real power exports from an area and the scheduled exports. But it has an additional term ACE = Pactual - Psched – 10b(freqact - freqsched)
b is the balancing authority frequency bias in MW/0.1 Hz with a negative sign. It is about 0.8% of peak load/generation
This slower ACE response is usually not modeled in transient stability

## Slide 28: Turbine Models
model shaft “squishiness” as a spring
High-pressure turbine shaft dynamics
Usually shaft dynamics are neglected

## Slide 29: Steam Turbine Models
Boiler supplies a "steam chest" with the steam then entering the turbine through a value
We are assuming d=dHP and w=wHP

## Slide 30: Steam Governor Model

## Slide 31: Steam Governor Model
R = .05 (5% droop)
Steam valve limits

## Slide 32: TGOV1 Model
Standard model that is close to this is TGOV1
About 12% of governors in a 2015 EI model are TGOV1;
R = 0.05, T1 is less than 0.5 (except a few 999’s!), T3 has an average of 7, average T2/T3 is 0.34; Dt is used to model turbine damping and is often zero (about 80% of time in EI)

## Slide 33: IEEEG1 Model
A common stream turbine model, is the IEEEG1, originally introduced in the below 1973 paper
IEEE Committee Report, “Dynamic Models for Steam and Hydro Turbines in Power System Studies,” Transactions in Power Apparatus & Systems, volume 92, No. 6, Nov./Dec. 1973, pp 1904-15
In this model K=1/R
It can be used to represent cross-compound units, with high and low pressure steam
Uo and Uc are rate limits

## Slide 34: IEEEG1
Blocks on the right model the various steam stages
About 12% of WECC and EI governors are currently IEEEG1s
Below figures show two test comparison with this model
Image Source: Figs 2-4, 2-6 of IEEE PES, "Dynamic Models for Turbine-Governors in Power System Studies," Jan 2013

## Slide 35: Deadbands
Before going further, it is useful to briefly consider deadbands, with two types shown with IEEEG1 and described in the 2013 IEEE PES Governor Report
The type 1 is an intentional deadband, implemented to prevent excessive response
  Until the deadband activates there is no response, then normal response after that; this can cause a potentially large jump in the response
  Also, once activated there is normal response coming back into range
  Used on input to IEEEG1

## Slide 36: Deadbands
The type 2 is also an intentional deadband, implemented to prevent excessive response
  Difference is response does not jump, but rather only starts once outside of the range
Another type of deadband is the unintentional, such as will occur with loose gears
  Until deadband "engages" there is no response
  Once engaged there is a hysteresis in the response
When starting simulations deadbands usually start at their origin

## Slide 37: Frequency Deadbands in ERCOT
In ERCOT NERC BAL-001-TRE-1 (“Primary Frequency Response in the ERCOT Region”) has the purpose “to maintain interconnection steady-state frequency within defined limits”
The deadband requirement is +/- 0.034 Hz for steam and hydro turbines with mechanical governors; +/- 0.017 Hz for all other generating units
The maximum droop setting is 5% for all units except it is 4% for combined cycle combustion turbines
Source: NERC BAL-001-TRE-1 and ERCOT, Demonstration of PFR Improvement, ERCOT Operations Planning, Sept. 2017 presentation

## Slide 38: Comparing ERCOT 2017 Versus 2008 Frequency Profile (5 mHz bins)

## Slide 39: Gas Turbines
A gas turbine (usually using natural gas) has a compressor, a combustion chamber and then a turbine
The below figure gives an overview of the modeling
Image from IEEE PES, "Dynamic Models for Turbine-Governors in Power System Studies," Jan 2013
HRSG is the heat recovery steam generator (if it is a combined cycle unit)

## Slide 40: GAST Model
Quite detailed gas turbine models exist; we'll just consider the simplest, which is still used some
It is somewhat similar to the TGOV1. T1 is for the fuel valve, T2 is for the turbine, and T3 is for the load limit response based on the ambient temperature (At);
T3 is the delay in measuring the exhaust temperature
T1 average is 0.9, T2 is 0.6 sec

## Slide 41: Play-in (Playback) Models
Often time in system simulations there is a desire to test the response of units (or larger parts of the simulation) to particular changes in voltage or frequency
  These values may come from an actual system event
"Play-in" or playback models can be used to vary an infinite bus voltage magnitude and frequency, with data specified in a file
PowerWorld allows both the use of files (for say recorded data) or auto-generated data
  Machine type GENCLS_PLAYBACK can play back a file
  Machine type InfiniteBusSignalGen can auto-generate a signal

## Slide 42: PowerWorld Infinite Bus Signal Generation
Below dialog shows some options for auto-generation of voltage magnitude and frequency variations
Start Time tells when to start; values are then defined for up to five separate time periods
Volt Delta is the magnitude of the pu voltage deviation; Volt Freq is the frequency of the voltage deviation in Hz (zero for dc)
Speed Delta is the magnitude of the frequency deviation in Hz; Speed Freq is the frequency of the frequency deviation
Duration is the time in seconds for the time period

## Slide 43: Example: Step Change in Voltage Magnitude
Below graph shows the voltage response for the four bus system for a change in the infinite bus voltage
Case name: B4_SignalGen_Voltage

## Slide 44: Example: Step Change Frequency Response
Graph shows response in generator 4 output and speed for a 0.1% increase in system frequency
This is a 100 MVA unit with a per unit R of 0.05

## Slide 45: Simple Diesel Model: DEGOV
Sometimes models implement time delays (DEGOV)
  Often delay values are set to zero
Delays can be implemented either by saving the input value or by using a Pade approximation, with a 2nd order given below; a 4th order is also common

## Slide 46: DEGOV Delay Approximation
With TD set to 0.5 seconds (which is longer than the normal of about 0.05 seconds in order to illustrate the delay)

## Slide 47: Hydro Units
Hydro units tend to respond slower than steam and gas units; since early transient stability studies focused on just a few seconds (first or second swing instability), detailed hydro units were not used
  The original IEEEG2 and IEEEG3 models just gave the linear response; now considered obsolete
Below is the IEEEG2; left side is the governor, right side is the turbine and water column
For sudden changes there is actually an inverse change in the output power

## Slide 48: Four Bus Example with an IEEEG2
Graph below shows the mechanical power output of gen 2 for a unit step decrease in the infinite bus frequency; note the power initially goes down!
Case name: B4_SignalGen_IEEEG2
This is caused by a transient decrease in the water pressure when the valve is opened to increase the water flow; flows does not change instantaneously because of the water’s inertia.

## Slide 49: Washout Filters
A washout filter is a high pass filter that removes the steady-state response (i.e., it "washes it out") while passing the high frequency response
They are commonly used with hydro governors and (as we shall see) with power system stabilizers
With hydro turbines ballpark values for Tw are around one or two seconds

## Slide 50: IEEEG3
This model has a more detailed governor model, but the same linearized turbine/water column model
Because of the initial inverse power change, for fast deviations the droop value is transiently set to a larger value (resulting in less of a power change)
Previously WECC had about 10% of their governors modeled with IEEEG3s; in 2019 it is about 5%
Because of the washout filter at high frequencies RTEMP dominates (on average it is 10 times greater than RPERM)

## Slide 51: Tuning Hydro Transient Droop
As given in equations 9.41 and 9.42 from Kundar (1994) the transient droop should be tuned so
Source: 9.2, Kundur, Power System Stability and Control, 1994
In comparing an average H is about 4 seconds, so TM is 8 seconds, an average TW is about 1.3, giving an calculated average RTEMP of 0.37 and TR of 6.3; the actual averages in a WECC case are 0.46 and 6.15. So on average this is pretty good! Rperm is 0.05

## Slide 52: IEEEG3 Four Bus Frequency Change
The two graphs compare the case response for the frequency change with different RTEMP values
RTEMP = 0.5, RPERM = 0.05
Case name: B4_SignalGen_IEEEG3
RTEMP = 0.05, RPERM = 0.05
Less variation

## Slide 53: Basic Nonlinear Hydro Turbine Model
Basic hydro system is shown below
  Hydro turbines work be converting the kinetic energy in the water into mechanical energy
  assumes the water is incompressible
At the gate assume a velocity of U, a cross-sectional penstock area of A; then the volume flow is A*U=Q;
Source: 9.2, Kundur, Power System Stability and Control, 1994

## Slide 54: Basic Nonlinear Hydro Turbine Model
From Newton's second law of motion the change in the flow volume Q
As per [a] paper, this equation is normalized to
[a] "Hydraulic Turbine and Turbine Control Models for System Dynamic Studies," IEEE Trans. Power Syst., Feb, 92
TW is called the water time constant, or water starting time

## Slide 55: Basic Nonlinear Hydro Turbine Model
With hbase the static head, qbase the flow when the gate is fully open, an interpretation of Tw is the time (in seconds) taken for the flow to go from stand-still to full flow if the total head is hbase
If included, the head losses, hloss, vary with the square of the flow
The flow is assumed to vary as linearly with the gate position (denoted by c)

## Slide 56: Basic Nonlinear Hydro Turbine Model
Power developed is proportional to flow rate times the head, with a term qnl added to model the fixed turbine (no load) losses
  The term At is used to change the per unit scaling to that of the electric generator

## Slide 57: Model HYGOV
This simple model, combined with a governor, is implemented in HYGOV
About 6% of WECC governors use this model; average TW is
2 seconds
The gate position (GV) to gate power (PGV) is sometimes represented with a nonlinear curve
Hloss is assumed small and not included