## Slide 1: ECEN 667 Power System Stability
Lecture 20: SMIB Eigenvalues, Measurement-Based Modal Analysis
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 8
Homework 6 is due on November 11
There is a 2019 NERC document on oscillations at www.nerc.com/comm/PC/SMSResourcesDocuments/Interconnection_Oscillation_Analysis.pdf

## Slide 3: Single Machine Infinite Bus
A quite useful analysis technique is to consider the small signal stability associated with a single generator connected to the rest of the system through an equivalent transmission line
Driving point impedance looking into the system is used to calculate the equivalent line's impedance
  The Zii value can be calculated quite quickly using sparse vector methods
Rest of the system is assumed to be an infinite bus with its voltage set to match the generator's real and reactive power injection and voltage

## Slide 4: Small SMIB Example
As a small example, consider the 4 bus system shown below, in which bus 2 really is an infinite bus
To get the SMIB for bus 4, first calculate Z44
Z44 is Zth in parallel with jX'd,4 (which is j0.3) so Zth is j0.22

## Slide 5: Small SMIB Example
The infinite bus voltage is then calculated so as to match the bus i terminal voltage and current
In the example we have
While this was demonstrated on an extremely small system for clarity, the approach works the same for any size system

## Slide 6: Calculating the A Matrix
The SMIB model A matrix can then be calculated either analytically or numerically
  The equivalent line's impedance can be embedded in the generator model so the infinite bus looks like the "terminal"
This matrix is calculated in PowerWorld by selecting Transient Stability, SMIB Eigenvalues
  Select Run SMIB to perform an SMIB analysis for all the generators in a case
  Right click on a generator on the SMIB form and select Show SMIB to see the Generator SMIB Eigenvalue Dialog
  These two bus equivalent networks can also be saved, which can be quite useful for understanding the behavior of individual generators

## Slide 7: Example: Bus 4 SMIB Dialog
On the SMIB dialog, the General Information tab shows information about the two bus equivalent
PowerWorld case B4_SMIB

## Slide 8: Example: Bus 4 SMIB Dialog
On the SMIB dialog, the A Matrix tab shows the Asys matrix for the SMIB generator
In this example A21 is showing

## Slide 9: Example: Bus 4 with GENROU
The eigenvalues can be calculated for any set of generator models
This example replaces the bus 4 generator classical machine with a GENROU model
  There are now six eigenvalues, with the dominate response coming from the electro-mechanical mode with a frequency of 1.84 Hz, and damping of 6.9%
PowerWorld case B4_GENROU_Sat_SMIB

## Slide 10: Example: Bus 4 with GENROU Model and Exciter
Adding an relatively slow EXST1 exciter adds additional states (with KA=200, TA=0.2)
  As the initial reactive power output of the generator is decreased, the system becomes unstable (below example is with a generator reactive power output of 0 Mvar)
PowerWorld case B4_GENROU_Sat_SMIB_QZero

## Slide 11: Example: Bus 4 with GENROU Model and Exciter
The below image shows the system response to a brief bus 4 self-clearing fault

## Slide 12: Example: Bus 4 with GENROU Model and Exciter
The remainder of the Eigenvalues page shows the participation factors for the various states in the modes

## Slide 13: SMIB Eigenvalues for TSGC_2000 Case
All the SMIB eigenvalues can be calculated quickly even for relatively large grids

## Slide 14: Saving a Two Bus Equivalent
PowerWorld makes it easy to save a two bus equivalent from the SMIB Eigenvalues page
  Right-click and select Save Two Bus Equivalent
As the name implies, the two bus equivalent is the generator connected to an infinite bus through its driving point impedance
Two bus equivalents provide a convenient way to track down at least some causes of instability issues

## Slide 15: Small Signal Analysis and Measurement-Based Modal Analysis
Small signal analysis has been used for decades to determine power system frequency response
  It is a model-based approach that considers the properties of a power system, linearized about an operating point
Measurement-based modal analysis determines the observed dynamic properties of a system
  Input can either be measurements from devices (such as PMUs) or dynamic simulation results
  The same approach can be used regardless of the measurement source
Focus in this section is on the measurement-based approach

## Slide 16: Ring-down Modal Analysis
Ring-down analysis seeks to determine the frequency and damping of key power system modes following some disturbance
There are several different techniques, with the Prony approach the oldest (from 1795); introduced into power in 1990 by Hauer, Demeure and Scharf
Regardless of technique, the goal is to represent the response of a sampled signal as a set of exponentially damped sinusoidals (modes)

## Slide 17: Where We Are Going: Extracting the Modes from Signals
The goal is to gain information about the electric grid by extracting modal information from its signals
  The frequency and damping of the modes is key
The premise is we’ll be able to reproduce a complex signal, over a period of time, as a set a of sinusoidal modes
  We’ll also allow for linear detrending

## Slide 18: Example: The Summation of two damped exponentials
This example was created by going from the modes to a signal
We’ll be going in the opposite direction (i.e., from a measured signal to the modes)

## Slide 19: Some Reasonable Expectations
Verifiable to show how well the modes match the original signal(s)
  We’ll show this
Flexible to handle between one and many signals
  We’ll go up to simultaneously considering 40,000 signals
Fast
  What is presented will be, with a discussion of the computational scaling
Easy to use
  This is software implementation specific; results shown here were done using the modal analysis tool integrated into PowerWorld Simulator (version 22)

## Slide 20: Example: One Signal
This could be any signal; image shows the result of the original signal (blue) and the reproduced signal (red)

## Slide 21: Verification: Linear Trend Line Only

## Slide 22: Verification: Linear Trend Line + One Mode

## Slide 23: Verification: Linear Trend Line + Two Modes

## Slide 24: Verification: Linear Trend Line + Three Modes

## Slide 25: Verification: Linear Trend Line + Four Modes

## Slide 26: Verification: Linear Trend Line + Five Modes
It is hard to tell a difference on this one, illustrating that modes manifest differently in different signals

## Slide 27: A Larger Example We’ll Finish With
Applying the developed techniques to the response of all 43,400 substation frequencies from an 110,000 bus electric grid(20 million plus values)

## Slide 28: Spatial Visualization of Frequency

## Slide 29: Measurement-Based Modal Analysis
There are a number of different approaches
The idea of all techniques is to approximate a signal, yorg(t), by the sum of other, simpler signals (basis functions)
  Basis functions are usually exponentials, with linear and quadratic functions used to detrend the signal
  Properties of the original signal can be quantified from basis function properties
    Examples are frequency and damping
  Signal is considered over time with t=0 as the start
Approaches sample the original signal yorg(t)

## Slide 30: Measurement-Based Modal Analysis
Vector y consists of m uniformly sampled points from yorg(t) at a sampling value of DT, starting with t=0, with values yj for j=1…m
  Times are then tj= (j-1)DT
  At each time point j, the approximation of yj is

## Slide 31: Measurement-Based Modal Analysis
Error (residual) value at each point j is
The closeness of the fit can be quantified using the Euclidean norm of the residuals
Hence we need to determine a and b

## Slide 32: Sampling Rate and Aliasing
The Nyquist-Shannon sampling theory requires sampling at twice the highest desired frequency
  For example, to see a 5 Hz frequency we need to sample the signal at a rate of at least 10 Hz
Sampling shifts the frequency spectrum by 1/T (where T is the sample time), which causes frequency overlap
This is known as aliasing, which can cause a high frequency signal to appear to be a lower frequency signal
  Aliasing can be reduced by fast sampling and/or low pass filters
Image: upload.wikimedia.org/wikipedia/commons/thumb/2/28/AliasingSines.svg/2000px-AliasingSines.svg.png

## Slide 33: One Solution Approach: The Matrix Pencil Method
There are several algorithms for finding the modes. We’ll use the Matrix Pencil Method
  This is a newer technique for determining modes from noisy signals (from about 1990, introduced to power system problems in 2005); it is an alternative to the Prony Method
  The Matrix Pencil Method is useful when there is signal noise
Given m samples, with L=m/2, the first step is to form the Hankel Matrix, Y such that
Reference: A. Singh and M. Crow, "The Matrix Pencil for Power System Modal Extraction," IEEE Transactions on Power Systems, vol. 20, no. 1, pp. 501-502, Institute of Electrical and Electronics Engineers (IEEE), Feb 2005.
This not a sparse matrix

## Slide 34: Algorithm Details, cont.
Then calculate Y’s singular values using an economy singular value decomposition (SVD)
The ratio of each singular value is then compared to the largest singular value sc; retain the ones with a ratio > than a threshold
  This determines the modal order, M
  Assuming V is ordered by singular values (highest to lowest), let Vp be then matrix with the first M columns of V
The computational complexity increases with the cube of the number of measurements!
This threshold is a value that can be changed; decrease it to get more modes.

## Slide 35: Aside: The Matrix Singular Value Decomposition (SVD)
The SVD is a factorization of a matrix that generalizes the eigen decomposition to any m by n matrix to produce where S is a diagonal matrix of the singular values
The singular values are non-negative, real numbers that can be used to indicate the major components of a matrix (the gist is they provide a way to decrease the rank of a matrix)
The original concept is more than
100 years old, but has found lots of recent applications

## Slide 36: Aside: SVD Image Compression Example
Image Source: www.math.utah.edu/~goller/F15_M2270/BradyMathews_SVDImage.pdf
Images can be represented with matrices. When an SVD is applied and only the largest singular values are retained the image is compressed.

## Slide 37: Matrix Pencil Algorithm Details, cont.
Then form the matrices V1 and V2 such that
  V1 is the matrix consisting of all but the last row of Vp
  V2 is the matrix consisting of all but the first row of Vp
Discrete-time poles are found as the generalized eigenvalues of the pair (V2TV1, V1TV1) = (A,B)
These eigenvalues are the discrete-time poles, zi with the modal eigenvalues then
The log of a complex number z=r is ln(r) + j
If B is nonsingular (the situation here) then the generalized eigenvalues are the eigenvalues of B-1A

## Slide 38: Matrix Pencil Method with Many Signals
The Matrix Pencil approach can be used with one signal or with multiple signals
Multiple signals are handled by forming a Yk matrix for each signal k using the measurements for that signal and then combining the matrices
The required computation scales linearly with the number of signals

## Slide 39: Matrix Pencil Method with Many Signals
However, when dealing with many signals, usually the signals are somewhat correlated, so vary few of the signals are actually need to be included to determine the desired modes
Ultimately we are finding
The a is common to all the signals (i.e., the system modes) while the b vector is signal specific (i.e., how the modes manifest in that signal)

## Slide 40: Quickly Determining the b Vectors
A key insight is from an approach known as the Variable Projection Method (from Borden, 2013) that for any signal k
A. Borden, B.C. Lesieutre, J. Gronquist, "Power System Modal Analysis Tool Developed for Industry Use," Proc. 2013 North American Power Symposium, Manhattan, KS, Sept. 2013
Where m is the number of measurements and n is the number of modes