## Slide 1: ECEN 667 Power System Stability
Lecture 24: Power System Stabilizers (PSSs)
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Announcements
Read Chapter 9
Homework 7 should be done before the second exam but need not be turned in

## Slide 3: Dynamic Models in the Physical Structure
Machine
Governor
Exciter
Load
Char.
Load
Relay
Line
Relay
Stabilizer
Generator
P, Q
Network
Network control
Loads
Load control
Fuel
Source
Supply control
Furnace and Boiler
Pressure control
Turbine
Speed control
V, I
Torque
Steam
Fuel
Electrical System
Mechanical System
Voltage Control
P. Sauer and M. Pai, Power System Dynamics and Stability, Stipes Publishing, 2006.

## Slide 4: Power System Stabilizer (PSS) Models

## Slide 5: Example PSS
An example single input stabilizer is shown below (IEEEST)
  The input is usually the generator shaft speed deviation, but it could also be the bus frequency deviation, generator electric power or voltage magnitude
VST is an input into the exciter
The model can be simplified by setting parameters to zero

## Slide 6: Another Single Input PSS
The PSS1A is very similar to the IEEEST Stabilizer and STAB1
IEEE Std 421.5 describes the common stabilizers

## Slide 7: 2000 Bus System Results With Stabilizers
The case has 334 IEEST stabilizers, all with the same parameters (which would not be the case in a real system)
Results are given for the previous generator drop contingency

## Slide 8: 2000 Bus System Results Without Stabilizers
Clearly the case is unstable; note the change in scale

## Slide 9: 2000 Bus System Results Without Stabilizers Movie
The techniques from the last lecture were used to quickly create a movie showing this frequency response

## Slide 10: Example Dual Input PSS
Below is an example of a dual input PSS (PSS2A)
  Combining shaft speed deviation with generator electric power is common
  Both inputs have washout filters to remove low frequency components of the input signals
In addition to exciters, IEEE Std 421.5 describes the common stabilizers

## Slide 11: Washout Filters and Lead-Lag Compensators
Two common attributes of PSSs are washout filters and lead-lag compensators
Since PSSs are associated with damping oscillations, they should be immune to slow changes. These low frequency changes are “washed out” by the washout filter; this is a type of high-pass filter.
Washout filter
Lead-lag compensators

## Slide 12: Washout Filter
The filter changes both the magnitude and angle of the signal at low frequencies
Image Source: www.electronics-tutorials.ws/filter/filter_3.html
The breakpoint frequency is when the phase shift is 45 degrees and the gain is -3 dB (1/sqrt(2))
A larger T value shifts the breakpoint to lower frequencies; at T=10 the breakpoint frequency is 0.016 Hz

## Slide 13: Washout Parameter Variation
The PSS2A is the most common stabilizer in both the 2015 EI and WECC cases. Plots show the variation in TW1 for EI (left) and WECC cases (right); for both the x-axis is the number of PSS2A stabilizers sorted by TW1, and the y-axis is TW1 in seconds

## Slide 14: Lead-Lag Compensators
For a lead-lag compensator of the below form with a <= 1 (equivalently a >= 1)
There is no gain or phase shift at low frequencies, a gain at high frequencies but no phase shift
Equations for a design maximum phase shift a at a frequency f are given

## Slide 15: Stabilizer Design
As noted by Larsen, the basic function of stabilizers is to modulate the generator excitation to damp generator oscillations in frequency range of about 0.2 to 2.5 Hz
  This requires adding a torque that is in phase with the speed variation; this requires compensating for the gain and phase characteristics of the generator, excitation system, and power system (GEP(s))
  We need to compensate for the phase lag in the GEP
The stabilizer input is often the shaft speed
Image Source: Figure 1 from Larsen, 1981, Part 1

## Slide 16: Stabilizer Design
T6 is used to represent measurement delay; it is usually zero (ignoring the delay) or a small value (< 0.02 sec)
The washout filter removes low frequencies; T5 is usually several seconds (with an average of say 5)
  Some guidelines say less than ten seconds to quickly remove the low frequency component
  Some stabilizer inputs include two washout filters
Image Source: IEEE Std 421.5-2016

## Slide 17: Stabilizer Design Values
With a washout filter value of T5 = 10 at 0.1 Hz (s = j0.2p = j0.63) the gain is 0.987; with T5 = 1 at 0.1 Hz the gain is 0.53
Ignoring the second order block, the values to be tuned are the gain, Ks, and the time constants on the two lead-lag blocks to provide phase compensation
  We’ll assume T1=T3 and T2=T4

## Slide 18: Stabilizer Design Phase Compensation
Goal is to move the eigenvalues further into the left-half plane
Initial direction the eigenvalues move as the stabilizer gain is increased from zero depends on the phase at the oscillatory frequency
  If the phase is close to zero, the real component changes significantly but not the imaginary component
  If the phase is around -45 then both change about equally
  If the phase is close to -90 then there is little change in the real component but a large change in the imaginary component

## Slide 19: Stabilizer Design Tuning Criteria
Eigenvalues moves as Ks increases
A practical method is to find KINST, then set KOPT as about 1/3 to ½ of this value
  KOPT is where the damping is maximized
  KINST is the gain at which sustained oscillations or an instability occur

## Slide 20: Stabilizer Design Tuning
Basic approach is to provide enhanced damping at desired frequencies; the challenge is power systems can experience many different types of oscillations, ranging from the high frequency local modes to the slower (< 1.0 Hz usually) inter-area modes
Usually the PSS should be set to compensate the phase so there is little phase lag at inter-area frequencies
  This can get modified slightly if there is a need for local stability enhancement
An approach is to first set the phase compensation, then tune the gain; this should be done at full output

## Slide 21: PSS2A Example Values
Based on about 1000 WECC PSS2A models
  T1=T3 about 64% of the time and T2=T4 about 69% of the time
  The next page has a plot of the T1 and T2 values; the average T1/T2 ratio is about 6.4

## Slide 22: Example T1 and T2 Values

## Slide 23: PSS Tuning Example
Open the case wscc_9bus_Start, apply the default dynamics contingency of a self-clearing fault at Bus 8.
Use Modal Analysis to determine the major modal frequency and damping

## Slide 24: PSS Tuning Example: Getting Initial Frequency and Damping
The Modal Analysis button provides quick access
  Easy access to plot data
  Frequency is 1.36 Hz with 5% damping

## Slide 25: PSS Tuning Example: We’ll Add PSS1As at Gens 2 and 3
To increase the generator speed damping, we’ll add PSS1A stabilizers using the local shaft speed as an input
First step is to determine the phase difference between the PSS output and the PSS input; this is the value we’ll need to compensate
This phase can be determined either analytically, actually testing the generator or using simulation results
  We’ll use simulation results

## Slide 26: PSS Tuning Example: Using Stabilizer Reference Signals
PowerWorld now allows reference sinusoidals to be easily played into the stabilizer input
  This should be done at the desired modal frequency
Modal analysis can then be used to quickly determine the phase delay between the input and the signal we wish to damp
Open the case wscc_9Bus_Stab_Test
  This has SignalStab stabilizers modeled at each generator; these models can play in a fixed frequency signal

## Slide 27: SignalStab Input and Results
Enable the SignalStab stabilizer at the bus 2 generator and run the simulation
  At time=0 the stabilizer receives a sinusoidal input with a magnitude of 0.05 and a frequency of 1.36 Hz

## Slide 28: PSS Tuning Example: Gen2 Reference Signal Results
Graph shows four signals at bus 2, including the stabilizer input and the generator’s speed
  The phase relationships are most important
  Use modal analysis to determine the exact phase values for the 1.36 Hz mode; analyze the data between 5 and 10 seconds

## Slide 29: PSS Tuning Example: 1.36 Hz Modal Values
The change in the generator’s speed is driven by the stabilizer input sinusoid, so it will be lagging. The below values show is lags by (-161+360) – (-81.0) = 280 degrees
  Because we want to damp the speed not increased it, subtract off 180 degrees to flip the sign. So we need 100 degrees of compensation; with two lead-lags it is 50 degrees each

## Slide 30: PSS Tuning Example: 1.36 Hz Lead-Lag Values
In designing a lead-lag of the form to have a specified phase shift of  at a frequency f
the value of a is
In our example with  = 50 then

## Slide 31: PSS Tuning Example: 1.36 Hz Lead-Lag Values
In designing a lead-lag of the form to have a specified phase shift of  at a frequency f
The value of a is
In our example with  = 50 then

## Slide 32: PSS Tuning Example: 1.36 Hz Lead-Lag Values
Hence T1=T3=0.321, T2=T4=0.042. We’ll assumed T6=0, and T5=10, and A1=A2=0
The last step is to determine Ks. This is done by finding the value of Ks at just causes instability (i.e., KINST), and then setting Ks to about 1/3 of this value
  Instability is easiest to see by plotting the output (VST) value for the stabilizer

## Slide 33: PSS Tuning Example: Setting the Values for Gen 2
Instability occurs with KS = 55, hence the optimal value is about 55/3=18.3
This increases the damping from 5% to about 16.7%
  This is saved as case WSCC_9bus_Stab

## Slide 34: PSS Tuning Example: Setting the Values for Gen 3
The procedure can be repeated to set the values for the bus 3 generator, where we need a total of 68 degrees of compensation, or 34 per lead-lag
The values are a = 0.283, T1=0.22, T2=0.062, KS for the verge of instability is 36, so KS optimal is 12.

## Slide 35: PSS Tuning Example: Final Solution
  With stabilizers at buses 2 and 3 the damping has been increased to 25.7%

## Slide 36: Example 2: Adding a PSS to a 42 Bus System
Goal is to try to improve damping by adding one PSS1A at a large generator at Lion345 (bus 42)
  Example event is a three-phase fault is applied to the middle of the 345 kV transmission line between Prairie (bus 22) and Hawk (bus 3) with both ends opened at 0.05 seconds
  The starting case name is Bus42_PSS

## Slide 37: Example 2: Decide Generators to Tune and Frequency
Generator speeds and rotor angles are observed to have a poorly damped oscillation around 0.6 Hz.

## Slide 38: Example 2: Response Quantified Using Modal Analysis
  For 0.6 Hz mode the damping is 2.89%

## Slide 39: Example 2: Determine Phase Compensation
Using a SignalStabStabilizer at bus 42 (Lion345), the phase lag of the generator’s speed, relative to the stabilizer input is 199 degrees; flipping the sign requires phase compensation of 19 degrees or 9.5 per lead-lag
Values are a = 0.72; for 0.6 Hz, T1= 0.313, T2=0.225; set T3 and T4 to match; gain at instability is about 450, so the gain is set to 150.
  The case with the test signal is Bus42_PSS_Test
  Adding this single stabilizer increases the damping to 4.24%

## Slide 40: Example 2: Determine Phase Compensation Other Gens
Adding and tuning three more stabilizers (at Grafton345 and the two units at Lake345) increases the damping to 8.16%
  However, these changes are impacting modes in other areas of the system

## Slide 41: Stability Phenomena and Tools
Large Disturbance Stability (Non-linear Model)
Small Disturbance Stability (Linear Model)
Structural Stability (Non-linear Model) Loss of stability due to parameter variations.
Tools
  Simulation
  Repetitive time-domain simulations are required to find critical parameter values, such as clearing time of circuit breakers.
  Direct methods using Lyapunov-based theory (Also called Transient Energy Function (TEF) methods)
    Can be useful for screening
  Sensitivity based methods.

## Slide 42: Transient Energy Function (TEF) Techniques
No repeated simulations are involved.
Limited somewhat by modeling complexity.
Energy of the system used as Lyapunov function.
Computing energy at the “controlling” unstable equilibrium point (CUEP) (critical energy).
CUEP defines the mode of instability for a particular fault.
Computing critical energy is not easy.

## Slide 43: Judging Stability / Instability
Stability is judged by Relative Rotor Angles.
Monitor Rotor Angles
(b) Stable
(a) Stable
(c) Unstable
(d) Unstable

## Slide 44: Mathematical Formulation
A power system undergoing a disturbance (fault, etc), followed by clearing of the fault, has the following model
  (1) Prior to fault (Pre-fault)
  (2) During fault (Fault-on or faulted)
  (3) After the fault (Post-fault)
X
X
Faulted
Post-Fault
(line-cleared)
Tcl is the clearing time

## Slide 45: Critical Clearing Time
Assume the post-fault system has a stable equilibrium point xs
All possible values of x(tcl) for different clearing times provide the initial conditions for the post-fault system
  Question is then will the trajectory of the post fault system, starting at x(tcl), converge to xs as t  
Largest value of tcl for which this is true is called the critical clearing time, tcr
The value of tcr is different for different faults

## Slide 46: Region of Attraction (ROA)
.
.
The region need not be closed; it can be open:
All faulted trajectories cleared before they reach the boundary of the ROA will tend to xs as t (stable)

## Slide 47: Methods to Compute RoA
Had been a topic of intense research in power system literature since early 1960’s.
The stable equilibrium point (SEP) of the post-fault system, xs, is generally close to the pre-fault EP, x0
Surrounding xs there are a number of unstable equilibrium points (UEPs).
The boundary of ROA is characterized via these UEPs

## Slide 48: Characterization of RoA
Define a scalar energy function V(x) = sum of the kinetic and potential energy of the post-fault system.
Compute V(xu,i) at each UEP, i=1,2,…
Defined Vcr as
  RoA is defined by V(x) < Vcr
  But this can be an extremely conservative result.
Alternative method: Depending on the fault, identify the critical UEP, xu,cr, towards which the faulted trajectory is headed; then V(x) < V(xu,cr) is a good estimate of the ROA.

## Slide 49: Lyapunov’s Method
Defining the function V(x) is a key challenge
Consider the system defined by
Lyapunov's method: If there exists a scalar function V(x) such that

## Slide 50: Ball in Well Analogy
The classic Lyapunov example is the stability of a ball in a well (valley) in which the Lyapunov function is the ball's total energy (kinetic and potential)
For power systems, defining a true Lyapunov function often requires using restrictive models
SEP
UEP
UEP

## Slide 51: Power System Example
Consider the classical generator model using an internal node representation (load buses have been equivalenced)
Cij are the susceptance terms, Dij the conductance terms

## Slide 52: Constructing the Transient Energy Function (TEF)
The reference frame matters. Either relative rotor angle formulation, or COI reference frame.
  COI is preferable since we measure angles with respect to the “mean motion” of the system.
TEF for conservative system (i.e., zero damping)
With center of speed as
where
We then transform the variables to the
COI variables as
It is easy to verify

## Slide 53: TEF
We consider the general case in which all Mi's are finite. We have two sets of differential equations:
Let the post fault system has a SEP at
This SEP is found by solving

## Slide 54: TEF
Steps for computing the critical clearing time are:
  Construct a Lyapunov (energy) function for the post-fault system.
  Find the critical value of the Lyapunov function (critical energy) for a given fault
  Integrate the faulted equations until the energy is equal to the critical energy; this instant of time is called the critical clearing time
Idea is once the fault is cleared the energy can only decrease, hence the critical clearing time is determined directly
Methods differ as to how to implement steps 2 and 3.

## Slide 55: Potential Energy Boundary Surface
Figure from course textbook