## Slide 1: ECEN 667 Power System Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu
Lecture 11: Exciter Modeling

## Slide 2: Announcements
Read Chapter 5; look at Appendix A
Homework 3 should be done before the first exam, but does not need to be turned in.
First exam is on Tuesday October 3 during class (except for the distance education students)
  It is closed-book and closed-notes, but one 8.5 by 11 inch hand written note sheet and calculators allowed
  My first exam from ECEN 667 in Fall 2021 has been posted to Canvas
1

## Slide 3: Block Diagram Basics
The following slides will make use of block diagrams to explain some of the models used in power system dynamic analysis. The next few slides cover some of the block diagram basics.
To simulate a model represented as a block diagram, the equations need to be represented as a set of first order differential equations
Also the initial state variable and reference values need to be determined
2

## Slide 4: Integrator Block
Equation for an integrator with u as an input and y as an output is
In steady-state with an initial output of y0, the initial state is y0 and the initial input is zero
u
y
3

## Slide 5: First Order Lag Block
Equation with u as an input and y as an output is
In steady-state with an initial output of y0, the initial state is y0 and the initial input is y0/K
Commonly used for measurement delay (e.g., TR block with IEEE T1)
u
y
Output of Lag Block
Input
4

## Slide 6: Derivative Block
Block takes the derivative of the input, with scaling KD and a first order lag with TD
  Physically we can't take the derivative without some lag
  An example is the feedback block in the IEEET1 model
In steady-state the output of the block is zero
State equations require a more general approach
u
y
5

## Slide 7: State Equations for More Complicated Functions
There is not a unique way of obtaining state equations for more complicated functions with a general form
To be physically realizable we need n >= m
6

## Slide 8: General Block Diagram Approach
One integration approach is illustrated in the below block diagram
Image source: W.L. Brogan, Modern Control Theory, Prentice Hall, 1991, Figure 3.7
7

## Slide 9: Derivative Example
Write in form
Hence b0=0, b1=KD/TD, a0=1/TD
Define single state variable x, then
Initial value of x is found by recognizing y is zero so x = -b1u
8

## Slide 10: Lead-Lag Block
In exciters such as the EXDC1 the lead-lag block is used to model time constants inherent in the exciter; the values are often zero (or equivalently equal)
In steady-state the input is equal to the output
To get equations write in form with b0=1/TB, b1=TA/TB, a0=1/TB
u
y
Output of Lead/Lag
input
The steady-state requirement that u = y is readily apparent
9

## Slide 11: Lead-Lag Block
The equations are with then
b0=1/TB, b1=TA/TB, a0=1/TB
10

## Slide 12: Limits: Windup versus Nonwindup
When there is integration, how limits are enforced can have a major impact on simulation results
Two major flavors: windup and non-windup
Windup limit for an integrator block
If Lmin  v  Lmax then y = v
else If v < Lmin then y = Lmin, else if v > Lmax then y = Lmax
u
y
Lmax
Lmin
v
The value of v is NOT limited, so its value can "windup" beyond the limits, delaying backing off of the limit
11

## Slide 13: Limits on First Order Lag
Windup and non-windup limits are handled in a similar manner for a first order lag
u
y
Lmax
Lmin
v
If Lmin  v  Lmax then y = v
else If v < Lmin then y = Lmin, else if v > Lmax then y = Lmax
Again the value of v is NOT limited, so its value can "windup" beyond the limits, delaying backing off of the limit
12

## Slide 14: Non-Windup Limit First Order Lag
With a non-windup limit, the value of y is prevented from exceeding its limit
Lmax
Lmin
u
y
13

## Slide 15: Lead-Lag Non-Windup Limits
There is not a unique way to implement non-windup limits for a lead-lag. This is the one from IEEE 421.5-1995 (Figure E.6)
T2 > T1, T1 > 0, T2 > 0
If y > B, then x = B
If y < A, then x = A
If B y  A, then x = y
14

## Slide 16: Ignored States
When integrating block diagrams often states are ignored, such as a measurement delay with TR=0
In this case the differential equations just become algebraic constraints
Example: For block at right, as T0, v=Ku
With lead-lag it is quite common for TA=TB, resulting in the block being ignored
u
y
Lmax
Lmin
v
15

## Slide 17: Brief Review of DC Machines
Prior to widespread use of machine drives, dc motors had a important advantage of easy speed control
On its stator a dc machine has either a permanent magnet or a single concentrated winding
Rotor (armature) currents are supplied through brushes and the commutator
Equations are
The f subscript refers to the field, the a to the armature; wm is the machine's speed, G is a constant. In a permanent magnet machine the field flux is constant, the field equation goes away, and the field impact is embedded in a equivalent constant to G if
Taken mostly from M.A. Pai, Power Circuits and Electromechanics
16

## Slide 18: Review of DC Machines
The purpose of the next few slides is to provide insight into the source of portions of the block diagrams for various types of exciters
17

## Slide 19: Types of DC Machines
If there is a field winding (i.e., not a permanent magnet machine) then the machine can be connected in the following ways
  Separately-excited: Field and armature windings are connected to separate power sources
    For an exciter, control is provided by varying the field current (which is stationary), which changes the armature voltage
  Series-excited: Field and armature windings are in series
  Shunt-excited: Field and armature windings are in parallel
18

## Slide 20: Separately Excited DC Exciter
(to the synchronous machine)
s1 is coefficient of dispersion, modeling the flux leakage
19

## Slide 21: Separately Excited DC Exciter
Relate the input voltage, ein1, to vfd
Assuming a constant speed w1
Solve above for ff1 which was used in the previous slide
20

## Slide 22: Separately Excited DC Exciter
If it was a linear magnetic circuit, then vfd would be proportional to in1; for a real system we need to account for saturation
Without saturation we can write
21

## Slide 23: Separately Excited DC Exciter
This equation is then scaled based on the synchronous machine base values
22

## Slide 24: Separately Excited Scaled Values
Thus we have
VR is the scaled output of the voltage regulator amplifier
23

## Slide 25: The Self-Excited Exciter
When the exciter is self-excited, the amplifier voltage appears in series with the exciter field
Note the additional Efd term on the end
24

## Slide 26: Self and Separated Excited Exciters
The same model can be used for both by just modifying the value of KE
25

## Slide 27: Exciter Model IEEET1 KE Values
Example IEEET1 Values from a large system
The KE equal 1 are separately excited, and KE close to zero are self excited
26

## Slide 28: Saturation
A number of different functions can be used to represent the saturation
The quadratic approach is now quite common
Exponential function could also be used
This is the same function used with the machine models
27

## Slide 29: Exponential Saturation
In Steady state
28

## Slide 30: Exponential Saturation Example
Given:
Find:
29

## Slide 31: Voltage Regulator Model
Amplifier
In steady state
As KA is increased
There is often a droop in regulation
Modeled as a first order differential equation
30

## Slide 32: Feedback
This control system can often exhibit instabilities, so some type of feedback is used
One approach is a stabilizing transformer
Designed with a large Lt2 so It2  0
31

## Slide 33: Feedback
32

## Slide 34: IEEET1 Model Evolution
The original IEEET1, from 1968, evolved into the EXDC1 in 1981
Image Source: Fig 3 of "Excitation System Models for Power Stability Studies," IEEE Trans. Power App. and Syst., vol. PAS-100, pp. 494-509, February 1981
1968
1981
Note, KE in the feedback is the same in both models
33

## Slide 35: IEEEX1
This is from 1979, and is the EXDC1 with the potential for a measurement delay and inputs for under or over excitation limiters
34

## Slide 36: IEEET1 Evolution
In 1992 IEEE Std 421.5-1992 slightly modified the EXDC1, calling it the DC1A (modeled as ESDC1A)
Image Source: Fig 3 of IEEE Std 421.5-1992
VUEL is a signal from an under- excitation limiter, which we'll cover later
Same model is in 421.5-2005
35

## Slide 37: IEEET1 Evolution
Slightly modified in Std 421.5-2016
Note the minimum limit on EFD
There is also the addition to the input of voltages from a stator current limiters (VSCL) or over excitation limiters (VOEL)
36

## Slide 38: IEEET1 Example
Assume previous GENROU case with saturation. Then add a IEEE T1 exciter with KA=50, TA=0.04, KE=-0.06, TE=0.6, VR,max=1.0, VR,min= -1.0 For saturation assume SE(2.8) = 0.04, SE(3.73)=0.33
Saturation function is 0.1621(EFD-2.303)2 (for EFD > 2.303); otherwise zero
EFD is initially 3.22
SE(3.22)*EFD=0.437
(VR-SE*EFD)/KE=EFD
VR =0.244
VREF = 0.244/Ka +VT =0.0488 +1.0946=1.09948
Case B4_GENROU_Sat_IEEET1
37

## Slide 39: IEEE T1 Example
For 0.1 second fault (from before), plot of EFD and the terminal voltage is given below
Initial V4=1.0946, final V4=1.0973
  Steady-state error depends on the value of KA
38

## Slide 40: IEEET1 Example
Same case, except with KA=500 to decrease steady-state error, no VR limits; this case is actually unstable
39

## Slide 41: IEEET1 Example
With KA=500 and rate feedback, KF=0.05, TF=0.5
Initial V4=1.0946, final V4=1.0957
40

## Slide 42: Combined EI/WECC Case Type 1 Exciters
In a recent combined EI/WECC case with about 11,000 exciters, 320 are modeled with the IEEE T1, 129 with IEEE X1, 147 with the EXDC1, and 162 with the ESDC1A
Graph shows KE value for the IEEE T1 exciters in case; about 1/4 are separately excited (KE =1, and the rest self excited
  A value of KE equal zero indicates code should set KE so Vr initializes to zero; this is used to mimic the operator action of trimming this value
41

## Slide 43: DC2 Exciters
Other dc exciters exist, such as the EXDC2, which is quite similar to the EXDC1
Image Source: Fig 4 of "Excitation System Models for Power Stability Studies," IEEE Trans. Power App. and Syst., vol. PAS-100, pp. 494-509, February 1981
Vr limits are multiplied by the terminal voltage
42

## Slide 44: ESDC4B
A newer dc model introduced in 421.5-2005 in which a PID controller is added; might represent a retrofit
Image Source: Fig 5-4 of IEEE Std 421.5-2005
43

## Slide 45: AC Exciters
Almost all new exciters use an ac source with an associated rectifier (either from a machine or static)
AC exciters use an ac generator and either stationary or rotating rectifiers to produce the field current
  In stationary systems the field current is provided through slip rings
  In rotating systems since the rectifier is rotating there is no need for slip rings to provide the field current
  Brushless systems avoid the anticipated problem of supplying high field current through brushes, but these problems have not really developed
44

## Slide 46: AC Exciter Modeling
  Originally represented by IEEE T2 shown below
Image Source: Fig 2 of "Computer Representation of Excitation Systems," IEEE Trans. Power App. and Syst., vol. PAS-87, pp. 1460-1464, June 1968
Exciter model is quite similar to IEEE T1; in the EI/WECC case there are 105 IEEE T2 exciters (about 1%)
45

## Slide 47: EXAC1 Exciter
The FEX function represent the rectifier regulation, which results in a decrease in output voltage as the field current is increased
Image Source: Fig 6 of "Excitation System Models for Power Stability Studies," IEEE Trans. Power App. and Syst., vol. PAS-100, pp. 494-509, February 1981
KD models the exciter machine reactance
About 1% of the EI/WECC exciters are EXAC1
46

## Slide 48: EXAC1 Rectifier Regulation
Image Source: Figures E.1 and E.2 of "Excitation System Models for Power Stability Studies," IEEE Trans. Power App. and Syst., vol. PAS-100, pp. 494-509, February 1981
There are about 6 or 7 main types of ac exciter models
Kc represents the commuting reactance
47

## Slide 49: Initial State Determination, EXAC1
To get initial states Efd and Ifd would be known and equal
Solve Ve*Fex(Ifd,Ve) = Efd
  Easy if Kc=0, then In=0 and Fex =1
  Otherwise the FEX function is represented by three piecewise functions; need to figure out the correct segment; for example for Mode 3
Need to check to make sure we are on this segment
48

## Slide 50: Static Exciters
In static exciters the field current is supplied from a three phase source that is rectified (i.e., there is no separate machine)
Rectifier can be either controlled or uncontrolled
Current is supplied through slip rings
Response can be quite rapid
49

## Slide 51: EXST1 Block Diagram
The EXST1 is intended to model rectifier in which the power is supplied by the generator's terminals via a transformer
  Potential-source controlled-rectifier excitation system
The exciter time constants are assumed to be so small they are not represented
This (and the related ESST1A) is a very common exciter (about 14% of EI/WECC total)
Kc represents the commuting reactance
50

## Slide 52: EXST4B
EXST4B models a controlled rectifier design; field voltage loop is used to make output independent of supply voltage
This (and the related ESST4B) are the most common exciters (about 20% of the total); Ve is almost always independent of IT
51

## Slide 53: Simplified Excitation System Model
A very simple model call Simplified EX System (SEXS) is available
  Not now commonly used; also other, more detailed models, can match this behavior by setting various parameters to zero
52

## Slide 54: Desired Performance
A discussion of the desired performance of exciters is contained in IEEE Std. 421.2-2014 (update from 1990)
Concerned with
  large signal performance: large, often discrete change in the voltage such as due to a fault; nonlinearities are significant
    Limits can play a significant role
  small signal performance: small disturbances in which close to linear behavior can be assumed
Increasingly exciters have inputs from power system stabilizers, so performance with these signals is important
53

## Slide 55: Transient Response
Figure shows typical transient response performance to a step change in input
Image Source: IEEE Std 421.2-1990, Figure 3
54

## Slide 56: Small Signal Performance
Small signal performance can be assessed by either the time responses, frequency response, or eigenvalue analysis
Figure shows the typical open loop performance of an exciter and machine in the frequency domain
Image Source: IEEE Std 421.2-1990, Figure 4
55