## Slide 1: ECEN 460 Power System Operation and Control Spring 2025
Lecture 6: Transmission Lines, Transformers, Per Unit
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Transmission Line Insulators
The overhead transmission distribution lines are bare conductors, so they need to be connected to the grounded towers using insulators
Different types of insulators are used depending on the application. Examples include
  Pin insulators for low voltage (up to 33 kV) applications
  Suspension insulators, which have a number of porcelain disks connected together, with each having about 11 kV of insulation
  Strain insulators, which are designed for corners, in which they have to handle the line strain; they are an assembly of suspension insulators
Image source: www.electricaleasy.com/2016/10/insulators-used-in-overhead-power-lines.html
Suspension and strain insulators
1

## Slide 3: Transmission Line Models: An Equivalent Circuit
Our current model of a transmission line is shown below
Units on z and y are
per unit length
2

## Slide 4: Propagation Constant, Characteristic and Surge Impedance
3

## Slide 5: Lossless Transmission Lines
4

## Slide 6: Lossless Transmission Lines
If P > SIL then line consumes
vars; otherwise line generates vars.
Derived in Chapter 5, but this derivation is not part of ECEN 460
5

## Slide 7: Velocity of Propagation in a Lossless line
Velocity of propagation is close to the speed of light, but slightly less
Switching dynamics (outside of 460, more 616)
6

## Slide 8: Equivalent Circuit Model
Next, we’ll quickly cover simplified ways to determine the parameters Z' and Y'
7

## Slide 9: Simplified Parameters
8

## Slide 10: Simplified Parameters, cont.

## Slide 11: Three Line Models
Once the parameters have been derived, the Long and Medium models are the same; on ECEN 460 we will almost exclusively be using the Medium Line Model
10

## Slide 12: Power Transfer in Short Lines
Often we'd like to know the maximum power that could be transferred through a short transmission line
V1
V2
+
+
-
-
I1
I1
Transmission
Line with Impedance Z
S12
S21
11

## Slide 13: Power Transfer in Lossless Lines
12

## Slide 14: Limits Affecting Max. Power Transfer
Thermal limits
  limit is due to heating of conductor and hence depends heavily on ambient conditions.
  For many lines, sagging is the limiting constraint.
  Newer conductors limit can limit sag, carrying more current and hence increasing the ratings for existing lines (once they are reconductored)
    for example, 3M has ACCR (Aluminum Conductor Composite Reinforced) with the outer wires composed of a hardened aluminum- zirconium alloy, and the core having fiber-reinforced metal; they have half the thermal expansion and can operate continuously above 200° C!
    Higher currents and operating temperatures mean higher losses!
  Trees grow, and many will eventually hit lines if they are planted under the line.
13
Image source: www.3m.com/3M/en_US/p/d/b00014620/

## Slide 15: Other Limits Affecting Power Transfer
Angle limits
  while the maximum power transfer occurs when line angle difference is 90 degrees, actual limit is substantially less due to multiple lines in the system
Voltage stability limits
  as power transfers increases, reactive losses increase as I2X. As reactive power increases the voltage falls, resulting in a potentially cascading voltage collapse.
In cables the higher charging capacitance, which increases with the length of the line, limits the amount of current that can be transferred through the line since some of the current is associated with the charging capacitance
  Cables can be very sensitive to overloads since it is more of a challenge to dissipate heat
14

## Slide 16: Transmission Line Series Compensation
One way to increase the transmission capacity of a transmission line that is limited by its reactance is to add series compensation
  Capacitors are placed in series with the transmission line
Image: https://www.bpa.gov/news/newsroom/Pages/Chief-engineers-reunite-reminisce-for-BPAs-75th.aspx
Image shows BPA series capacitors in a 500 kV line
Subsynchronous oscillations can be a concern; the natural frequency of a series LC circuit is given below; in the right equation where f0 is the system frequency
15

## Slide 17: Transformers Overview
Power systems are characterized by many different voltage levels, ranging from 765 kV down to 240/120 volts.
Transformers are used to transfer power between different voltage levels.
The ability to inexpensively change voltage levels is a key advantage of ac systems over dc systems.
In this section we’ll development models for the transformer and discuss various ways of connecting three phase transformers.
16

## Slide 18: Transmission to Distribution Transformer
17

## Slide 19: Transmission Level Transformer
18

## Slide 20: Ideal Transformer
First we review the voltage/current relationships for an ideal transformer
  no real power losses
  magnetic core has infinite permeability
  no leakage flux
We’ll define the “primary” side of the transformer as the side that usually takes power, and the secondary as the side that usually delivers power.
  primary is usually the side with the higher voltage, but may be the low voltage side on a generator step-up transformer.
19

## Slide 21: Ideal Transformer Relationships
20

## Slide 22: Current/Voltage Relationships
21

## Slide 23: Impedance Transformation Example
Example: Calculate the primary voltage and current for an impedance load on the secondary
22

## Slide 24: Real Transformers
Real transformers
  have losses
  have leakage flux
  have finite permeability of magnetic core
Real power losses
  resistance in windings (i2 R)
  core losses due to eddy currents and hysteresis
23

## Slide 25: Transformer Core losses
Eddy currents arise because of changing flux in core.
Eddy currents are reduced by laminating the core
Hysteresis losses are proportional to area of BH curve and the frequency
These losses are reduced by using material with a thin BH curve
24
Image: en.wikipedia.org/wiki/Transformer_types#/media/File:Transformer.filament.agr.jpg

## Slide 26: Simplified Equivalent Circuit
Often the shunt elements are assumed to have such high impedance that they are ignored
25

## Slide 27: Calculation of Model Parameters
The parameters of the model are determined based upon
  nameplate data: gives the rated voltages and power
  open circuit test: rated voltage is applied to primary with secondary open; measure the primary current and losses (the test may also be done applying the voltage to the secondary, calculating the values, then referring the values back to the primary side).
  short circuit test: with secondary shorted, apply voltage to primary to get rated current to flow; measure voltage and losses.
This topic is mostly outside the scope of ECEN 460, covered in ECEN 459

## Slide 28: Residential Distribution Transformers
Single phase transformers are commonly used in residential distribution systems. Most distribution systems are 4 wire, with a multi-grounded, common neutral.
Image: www.osha.gov/dte/library/electrical/electrical_10.gif

## Slide 29: Load Tap-Changing Transformers
LTC transformers have tap ratios that can be varied to regulate bus voltages
  Sometimes called on-load tap-changing transformers (OLTCs) or under-load tap-changing transformers (ULTCs); on the distribution system called voltage regulators
The typical range of variation is 10% from the nominal values, usually in 33 discrete steps (0.0625% per step).
Because tap changing is a mechanical process, LTC transformers usually have a time delay deadband to avoid repeated changes (e.g., 30 seconds)

## Slide 30: Lab Three LTC Example
29

## Slide 31: LTCs and Circulating Vars
Unbalanced transformer taps can cause large amounts of reactive power to circulate, increasing power system losses and overloading transformers
30

## Slide 32: Phase Shifting Transformers (PSTs)
Phase shifting transformers are used to control the phase angle across the transformer
  Also called phase angle regulators (PARs) or quadrature booster transformers (British usage)
Since power flow through the transformer depends upon phase angle, this allows the transformer to regulate the power flow through the transformer
Phase shifters can be used to prevent inadvertent "loop flow" and to prevent line overloads.
I believe there are nine PSTs in ERCOT
Image Source: en.wikipedia.org/wiki/Quadrature_booster#/media/File:Qb-3ph.svg
31

## Slide 33: Phase Shifter Example 3.13
32

## Slide 34: Phase Shifter Example: Lake Erie Loop Flow
There are five phase shifters (called phase angle regulators [PARs] here) at the border between Michigan and Ontario. They are used to control how much electricity travels between the US and Canada
By adjusting the PARs the flow of electricity that “loops” around Lake Erie can be controlled
Source: MISO Board of Directors Market Committee Update, 9/30/13

## Slide 35: Lab Three Phase Shifter Example
34

## Slide 36: Per Unit Calculations
A key problem in analyzing power systems is the large number of transformers.
  It would be very difficult to continually have to refer impedances to the different sides of the transformers
This problem is avoided by a normalization of all variables.
This normalization is known as per unit analysis.

## Slide 37: Per Unit Conversion Procedure, Single-Phase
Pick a single-phase VA base for the entire system, SB
Pick a voltage base for each different voltage level, VB. Voltage bases are related by transformer turns ratios. Voltages are line to neutral.
Calculate the impedance base, ZB= (VB)2/SB
Calculate the current base, IB = VB/ZB
Convert actual values to per unit
Note, per unit conversion on affects magnitudes, not the angles. Also, per unit quantities no longer have units (i.e., a voltage is 1.0 p.u., not 1 p.u. volts)

## Slide 38: Per Unit Solution Procedure
Convert to per unit (p.u.) (many problems are already in per unit)
Solve
Convert back to actual as necessary

## Slide 39: Per Unit Example
Solve for the current, load voltage and load power in the circuit shown below using per unit analysis with an SB of 100 MVA, and voltage bases of 8 kV, 80 kV and 16 kV
Same circuit, with
values expressed
in per unit.

## Slide 40: Per Unit Example, cont’d

## Slide 41: Per Unit Example, cont’d
To convert back to actual values just multiply the per unit values by their per unit base

## Slide 42: Procedure for Balanced Three-Phase Circuits
Pick a 3f VA base for the entire system,
Pick a voltage base for each different voltage level, VB. Voltages are line to line.
Calculate the impedance base
Procedure is very similar to single-phase except we use a three-phase VA base, and use line to line voltage bases
Exactly the same impedance bases as with single phase!

## Slide 43: Three-Phase Per Unit, cont'd
Calculate the current base, IB
Convert actual values to per unit

## Slide 44: Three-Phase Per Unit Example
Solve for the current, load voltage and load power in the previous circuit, assuming a 3f power base of 300 MVA, and line to line voltage bases of 13.8 kV, 138 kV and 27.6 kV (square root of 3 larger than the 1f example voltages). Also assume the generator is Y-connected so its line to line voltage is 13.8 kV.
Convert to per unit
as before. Note the
system is exactly the
same!

## Slide 45: Three-Phase Per Unit Example, cont.
Again, analysis is exactly the same!

## Slide 46: Three-Phase Per Unit Example, cont'd
Differences appear when we convert back to actual values

## Slide 47: Three-Phase Per Unit Example 2
Assume a three-phase load of 100+j50 MVA with VLL of 69 kV is connected to a source through the below network:
What is the supply current and complex power?
Answer: I=467 amps, S = 103.3 + j76.0 MVA

## Slide 48: Per Unit Change of MVA Base
Parameters for equipment are often given using power rating of equipment as the MVA base
To analyze a system all per unit data must be on a common power base

## Slide 49: Transformer Reactance
Transformer reactance is often specified as a percentage, say 10%. This is a per unit value (divide by 100) on the power base of the transformer.
Example: A 350 MVA, 230/20 kV transformer has leakage reactance of 10%. What is p.u. value on 100 MVA base? What is value in ohms (230 kV)?
48