## Slide 1: ECEN 460 Power System Operation and Control Spring 2025
Lecture 17: Power System Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu

## Slide 2: Design Project Overview
The goal of the project is to give experience in planning new transmission for a relatively large-scale electric grid while working as part of a four person engineering design team
Project is motivated by the July 2024 ERCOT report to plan for new transmission in the Permian Basin to accommodate large amounts of new load

## Slide 3: Design Project Overview, cont.
Since the actual grid models are not publicly available due to them being CEII, you’ll be working with an enhanced version of the 2000 bus grid we’ve been using in 460
  This enhanced grid has much more wind and solar and a higher load; this grid uses at 500/230/161/115 kV transmission grid
Your design goal is to optimally provide reliable electricity to 5 new loads in (or close to) the Permian Basin, with each load requiring 1000 MW at 161 kV
There will be a number of assumptions to simplify the project, including using a DC OPF, only considering three distinct operating points, and ignoring all contingencies except those associated with your new transmission lines and transformers

## Slide 4: Design Project Overview: Starting Grid Flows and Generation by Fuel Type
3
Available generation by fuel type (black-coal, orange-natural gas, red-nuclear, green-wind, yellow-solar, blue-hydro)

## Slide 5: Design Project Overview: Starting Grid Flows and Generation by Fuel Type
Supply Curve

## Slide 6: Existing and New Load
This image shows the existing load, with the rectangles proportional to the load
The five large rectangles towards the left represent the new, currently not connected, load

## Slide 7: You are Encouraged to Read the ERCOT Report
It will be included with the design project. This image is a solution presented in the report. However, they are designing for the existing 345/138 kV grid, not your 500/161 kV grid
The ERCOT report is estimating costs on the order of $ 13 billion

## Slide 8: Back to Stability: The Frequency Contour Videos for the West and East from Last Lecture
Video is FreqMovie_WECC
Video is FreqMovie_East

## Slide 9: Longer Term Frequency Recovery
Normally the frequency recovers in about ten minutes

## Slide 10: ERCOT Winter Storm Uri Frequency (2/15/21)
Image source: https://www.ercot.com/files/docs/2021/03/03/Texas_Legislature_Hearings_2-25-2021.pdf

## Slide 11: Generator Under and Over Frequency Protection
Generators have automatic protection systems to trip them if the frequency goes out of range for too long (also their voltage)
A typical concern with off-nominal frequency operation is the turbine (i.e., not the synchronous machine) operating at close to one of its natural frequencies, resulting in accelerated aging (metal fatigue); this is often shown using a Campbell diagram; see IEEE C37.106.2022
NERC Standard PRC-024.1

## Slide 12: 2000 Bus Generator Outage Example
To do an example larger case generator drop stability study, open the case Texas2000_GenDrop
  Case has 67,000 MW of load; contingency is the loss of a 1350 MW generator
  Go to the Transient Stability form and click Run Transient Stability
  Rerun but drop two generators (one event is initially disabled)
1350 MW loss
2700 MW loss

## Slide 13: Generator Transient Stability Models
In order to study the transient response of a power system we need to develop models for the generator valid during the transient time frame of several seconds following a system disturbance
We need to develop both electrical and mechanical models for the generators
With the models, we’re starting here

## Slide 14: Generator Electrical Model
The simplest generator model, known as the classical model, treats the generator as a voltage source behind the direct-axis transient reactance; the voltage magnitude is fixed, but its angle changes according to the mechanical dynamics
This is an old model that is no longer used in practice, but is a good place to start

## Slide 15: Generator Mechanical Model
Generator Mechanical Block Diagram

## Slide 16: Generator Mechanical Model, cont’d
Constant mechanical power is no longer used in studies, but it is a good place to start

## Slide 17: Generator Mechanical Model, cont’d

## Slide 18: Generator Mechanical Model, cont’d

## Slide 19: Generator Swing Equation

## Slide 20: Single Machine Infinite Bus (SMIB)
To understand the transient stability problem we’ll first consider the case of a single machine (generator) connected to a power system bus with a fixed voltage magnitude and angle (known as an infinite bus) through a transmission line with impedance jXL

## Slide 21: SMIB, cont’d

## Slide 22: SMIB Equilibrium Points

## Slide 23: Transient Stability Analysis
For classical transient stability analysis we need to consider three systems
  Prefault - before the fault occurs the system is assumed to be at an equilibrium point
  Faulted - the fault changes the system equations, moving the system away from its equilibrium point
  Postfault - after fault is cleared the system hopefully returns to a new operating point
Actual stability studies can have multiple events and can be much more involved; however, this is a good place to start

## Slide 24: Transient Stability Solution Methods
There are two methods for solving the transient stability problem
  Direct or energy methods; for a two bus system this method is known as the equal area criteria
    mostly used to provide an intuitive insight into the transient stability problem
  Numerical integration
    this is by far the most common technique, particularly for large systems; during the fault and after the fault the power system differential equations are solved using numerical methods
23

## Slide 25: SMIB Direct Method Example
Assume a generator is supplying power to an infinite bus through two parallel transmission lines. Then a balanced three phase fault occurs at the terminal of one of the lines. The fault is cleared by the opening of this line’s circuit breakers.

## Slide 26: SMIB Example, cont’d
Simplified prefault system

## Slide 27: SMIB Example, Faulted System
During the fault the system changes
The equivalent system during the fault is then
During this fault (i.e., a balanced three-phase one) no power can be transferred from the generator to the system
26

## Slide 28: SMIB Example, Post Fault System
After the fault the system again changes
The equivalent system after the fault is then

## Slide 29: SMIB Example, Dynamics

## Slide 30: Equal Area Criteria
The goal of the equal area criteria is to try to determine whether a system is stable or not without having to completely integrate the system response.
System will be stable after the fault if the deceleration (Decel) area is greater than the acceleration (Accel.) area
29

## Slide 31: Example 12.4: Undamped
Assume there is a balanced three-phase fault at Bus 1, meaning that during the fault no power can be transferred from the generator to the rest of the system.
30

## Slide 32: Examples 12.4 and 5: Equal Area
The critical clearing time is slightly less than 0.19 seconds
31