## Slide 1: Enhancing the Resilience and Sustainability of Electric Grids
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
Texas A&M University
overbye@tamu.edu
April 8, 2025

## Slide 2: Greetings from the Texas A&M Electric Power Group
This is from our last semester dinner, held at Prof. Kate Davis’s house in September 2024

## Slide 3: Overview
Our modern society depends on a reliable electric grid with 40% of our energy transported in the form of electricity including most renewables
Blackouts are costly, with some estimates of costs above$100 billion/year in the US.
  Growing risk of catastrophic, long-term blackouts
  Blackouts cannot be completely eliminated, but risk and impact can be reduced with a more resilient grid
The electric grid is coupled with many other infrastructures and with the weather, and these couplings are becoming even stronger

## Slide 4: Quick Electric Grid Overview
Generation – source of electric energy
  Coal had provided over half of the U.S. electric energy, but now natural gas leads, with renewable sources rapidly growing
Load – consumes electric energy
  Consumers are in complete control of the switch; utilities must supply enough power to meet load
Transmission and Distribution – the wires that carry the power from generation to load
  Operating at voltages up to 765 kV (kilovolt), with 500 kV, 345 kV, 230 kV 161 kV and 138 kV common
Image source is US DOE, www.energy.gov/indianenergy/articles/united-states-electricity-industry-primer

## Slide 5: Synchronous Electric Grids Worldwide
Much of the electricity in the developed world is supplied by large-scale, 60 or 50 Hz synchronous electric grids
  Such grids can provide improved reliability, larger electricity markets and often economics of scale
  However, they add planning complexities
  Power can be transferred between synchronous grids by first converting it to dc, with HVDC lines one example
Islands, and other parts of the world are supplied by smaller electric grids
Large-Scale Electric Grid Interconnections
Image source: upload.wikimedia.org/wikipedia/commons/1/1c/Wide_area_synchronous_grid_%28Eurasia%2C_Mediterranean%29.png

## Slide 6: A Nice Visualization of Worldwide Electric Grids
The website openinframap.org visualizes the worldwide electric grid information contained in the OpenStreetMap database

## Slide 7: US Electricity Generation
Natural Gas (43.0%) and nuclear (17.8%) are most common sources, followed by coal (14.7%), wind (10.3), solar (7.0) and hydro (5.5%)
  Wood and other biomass is 1.1%, geothermal 0.3 %
  Coal was at least 50% of the total up to 2007
New construction mostly wind, solar and natural gas (with wind and solar energy costs now quite low)
When looking at predictions keep in mind the Yogi Berra quote, “It’s tough to make predictions, especially about the future”
US Generator Capacity Additions
Sources are by energy (not capacity), source US EIA, January 2025

## Slide 8: US Generation (November 2024) by Fuel Type
The sources variety substantially by state, the below image shows the change in the ERCOT (Texas) generation

## Slide 9: Important Electric Grid Considerations
Electricity cannot be economically stored
  In an interconnect generation must be continually adjusted to match changes in electric load and losses; this is gradually changing with more battery storage
Electric power flows on high voltage transmission lines cannot usually be directly controlled
  Control is mostly indirect, by changing generation
Customers have been in control of their load
Transmission system has finite limits; often operated close to its limit for economic reasons
The rapid growth in renewables is adding additional weather couplings

## Slide 10: Reliability and Resiliency
Keeping the lights on involves designing and operating the electric grid with a goal of simultaneously increasing two related but ultimately different concepts: reliability and resiliency
Reliability: suitable or fit to be relied on: dependable
  One of the key benefits of interconnected electric grids
Resiliency: an ability to recover from or adjust easily to misfortune or change
  A key focus of electric grid protection systems almost from day one, but there is a more recent focus on acknowledging that large-scale blackouts cannot be totally prevented, so we must be able to bounce back
9

## Slide 11: High-Impact, Low-Frequency Events
In order to enhance electric grid resiliency we need to consider the almost unthinkable events
These include what the North American Electric Reliability Corporation (NERC) calls High-Impact, Low-Frequency Events (HILFs); others call them black sky days, or severe resiliency events (SREs)
  Large-scale, potentially long duration blackouts
  HILFs identified by NERC were 1) a coordinated cyber, physical or blended attacks, 2) pandemics, 3) geomagnetic disturbances (GMDs), and 4) HEMPs
Image Source: NERC, 2012

## Slide 12: A Benign, Slightly High Impact, Low Frequency Event
There was a total eclipse on April 8, 2024 that passed over much of the US; in March we released a video showing the estimated impact on US PV generation

## Slide 13: What is Grid Resilience?
Merriam Webster Dictionary (resilience in general)
  “An ability to recover from or adjust easily to misfortune or change”
EPRI & North American Transmission Forum (NATF)
  The ability of the system and its components (… equipment and human …) to minimize damage and improve recovery from non-routine disruptions, including High Impact, Low Frequency (HILF) events, in a reasonable amount of time”
The impact of blackouts is not linear!
  Having 100 million people out of service can be more than tens times worse than 10 million out. A ten day blackout can be more than tens times worse than a one day blackout.
These definitions are from the 53rd North American Power Symposium keynote address by Dan Smith of Lower Colorado River Authority, November 2021

## Slide 14: Reliability – Resilience Continuum
Slide is from the 53rd North American Power Symposium keynote address by Dan Smith of Lower Colorado River Authority, November 2021; credit NATF

## Slide 15: Resilient to What?
A key question on resiliency is to determine the likely threats
  Some are geographic, and may are hard to quantify
Earthquake Risk
Source: Enhancing the Resilience of the Nation’s Electricity System, 2017
Freezing Rain Risk
The impact of wind and solar output on the weather is also a growing concern

## Slide 16: Resilient to What?
Electric grids are complex, and they are subject to a wide variety of different disturbances. Many occur regularly and some have never occurred
The image shows the frequency of US bulk outages from 1984-2015; large events are more common than an exponential distribution would indicate
Blackouts have been shown to have a power-law distribution so there is scale invariance

## Slide 17: Aside: Power Law Distributions
When considering a phenomena, it is useful to known 1) does it follow a power law, 2) if so over what range, and 3) what is it’s a exponent
Images Source: www-personal.umich.edu/~mejn/courses/2006/cmplxsys899/powerlaws.pdf
There is not a well defined average if a is less than 2
With power laws, extremes are more frequent than we expect

## Slide 18: Some Electric Grid Risks
Source: Enhancing the Resilience of the Nation’s Electricity System, 2017

## Slide 19: Major Considerations with Resiliency
Understanding, and ultimately enhancing resiliency, requires consideration during three periods
  Prior to an event
  During an event
  After an event
All three require planning ahead of time and flexibility as events unfold
This is presented as Figure 1.2a in the National Academies’ Enhancing the Resilience of the Nation’s Electricity System report (2017), and is originally from
S.E. Flynn, “America the resilient: Defying terrorism and mitigating
natural disasters.” Foreign Affairs, vol. 87: 2–8 (2008) and as illustrated by the National Infrastructure Advisory Council (NIAC) in 2010.

## Slide 20: How to Approach HILF Events
The goal in studying HILFs is seldom to replicate a specific event
  Many have not occurred, and within each class there can be great variability (e.g., a physical attack)
Nor is it to ensure there is no loss of service
Rather, it is to be broadly prepared, and to be able to do at least a reasonable cost/benefit analysis
HILF simulations can help in preparing for the unexpected
Several techniques, such as improved control room rare event situational awareness and better black start procedures, are generally applicable

## Slide 21: Challenges
An all hazards approach to considering resiliency is crucial, but there is no a “one-size-fits-all” solution
Identifying particular strategies to improve resiliency, to at least some degree, is relatively easy
The challenge is developing appropriate priorities for actions, and determining the appropriate political and organizational support to make it happen
  Just expecting electric utilities to make the investments necessary, while many are losing customer revenue to self-generation, might not be realistic
HILFs (or perhaps Severe Resiliency Events [SREs] is better) come in a continuum of frequencies and impacts

## Slide 22: Examples of Larger-Scale or Long Duration Outages
Quebec geomagnetic disturbance blackout of 1989
Auckland, NZ 1998 five week blackout due to cable failures
Northeast ice storm of 1998: A week long ice storm that resulted in more than three inches of ice on high voltage transmission lines, causing the collapse of 770 transmission towers and the replacement of 26,000 distribution poles

## Slide 23: Examples of Larger-Scale or Long Duration Outages, cont.
Northeast blackout from August 14, 2003
Hurricane Katrina (2005) with loss of service to 2.7 million customers, with 250,000 still out after 4 weeks
Superstorm Sandy (2012) with more than 8 million customers out, and about 10% still out after ten days
Cyber attack on Ukrainian Electric Grid (2015)
Hurricane Maria (2017) in Puerto Rico, with essentially a total loss of the grid
Image Source: IEEE Spectrum, P. Fairley, “Why Solar Microgrids May Fall Short in Replacing the Caribbean’s Devastated Power Systems”, October 2017

## Slide 24: May 10 to 13, 2024 Geomagnetic Disturbance (GMD)
A fairly large GMD caused just barely visible northern lights as far south as College Station, TX (latitude of 30.6)
While the Kp-index went up to its max value (9), it was not an overly severe GMD
  nT/minute of < 100, where 500 would be a 1989 event, and 2500 for Carrington
It caused more grid impacts than expected
Image: transmission.bpa.gov/Business/Operations/gic/gic.aspx

## Slide 25: HILF Two Main Categories
HILF events can be divided into two broad categories: 1) those not caused by human agents, and 2) those caused by human agents
Modeling the non-human events is somewhat easier because the goal is to (at least generally) replicate what has occurred, or what could occur
With human agent events the challenge is to protect the grid from potential events, without exposing vulnerabilities to an adversary or giving out potential mechanisms of attack
Synthetic grids are good for both

## Slide 26: Synthetic Electric Grids
Synthetic electric grids are completely fictional grids that have the characteristics and complexities of actual grids
Synthetic grids are very helpful for resiliency research since they allow algorithms to be developed and tested without revealing vulnerabilities of actual grids
Over the last ten years there has been tremendous progress on developing high-quality, geographically-based synthetic grids, with much of this work funded by ARPA-E and some by NSF
Still more work is needed, particularly for modeling the grid in the stability time frame, and in representing the protection systems

## Slide 27: 82K Synthetic Grid Covering the Contiguous US
The different colors indicate different nominal kV voltages, with green 765, orange 500, red 345, blue 230, black lower.
This grid has stability models
The grid does need to be updated, in part because when it was built the amount of renewable generation was much lower than today

## Slide 28: Electric Grid Resiliency Modeling Challenges
When considering resiliency events stability-level models often need to be used; this requires considering many different types of models
  We’re doing a study modeling a combined East-West grid, and it has 250 types of models
The grid’s operating point is constantly changing including the load, and generator and line/transformer statuses
Top Image: Sauer, P.W., M. A. Pai, Power System Dynamics and Stability, Stripes Publishing, 2007

## Slide 29: General Grid Resilience Comments
Understanding resilience requires considering how grids will respond to particular disturbances
Substantially changing the topologies of existing grids is not an option
In contrast to cyber security, there are seldom easy “patches” that can be applied to fix vulnerabilities
Simplistic studies of how a grid disturbance could cascade often lead to incorrect conclusions; sequential power flows, sequentially taking out overloaded devices are not particularly helpful
Full detail models of large-scale actual grids including the protection system usually don’t exist and modeling them would requiring knowing the associated remedial action schemes

## Slide 30: Economic Valuation of Resilience
While certainly challenging, metrics are needed to help determine the value of resilience to society
  If we need to improve resiliency, someone needs to pay
This is becoming a more challenging problem as more customers provide self-generation
  Is the ability of some customers to self generate, at least for a period of time, a net gain to the grid’s resiliency? How does one assess the resiliency of their systems?
Given that both reliability and resilience are often desired, their needs to be a co-optimization of their benefits.

## Slide 31: Example: Renewable Resource Droughts
With the rapid growth in wind and solar resources, a growing concern is how to handle wind and solar “droughts” with the generic term of renewable resource droughts used to describe them
The below example is a wind drought that occurred in the Midwest in late January 2020

## Slide 32: Example: Geomagnetic Disturbances (GMDs)
GMDs are caused by solar corona mass ejections (CMEs), and range from minor and frequent to severe and extremely rare
A GMD caused a blackout in 1989 of Quebec
They have the potential to severely disrupt the electric grid by causing quasi-dc geomagnetically induced currents (GICs) in the high voltage grid
Until recently power engineers had few tools to help them assess the impact of GMDs
GMD assessment tools are now moving into the realm of power system planning and operations engineers
31

## Slide 33: GMDs and the Kp-index
The earth’s magnetic field is constantly changing, though usually the variations are not significant
  Larger changes tend to occur closer to the earth’s poles
  The variation can be expressed different ways, such as nT/minute field variation
The magnitude of the variation at any particular location is quantified with a K-index
  Ranges from 0 to 9, with the value dependent on nT variation in horizontal direction over a three hour period; higher values are more severe
  This is station specific; higher variations are required to get a k=9 closer to the poles
The Kp-index is a weighted average of individual station K-indices; the G scale values are Kp – 4, so they have a maximum of 5.

## Slide 34: Electric Fields and Geomagnetically Induced Currents (GICs)
The induced electric field at the surface is dependent on deep earth (hundreds of km) conductivity
  Electric fields are vectors (magnitude and angle); values expressed in units of volts/mile (or volts/km);
  A 2500 nT/minute storm could produce 5 to 10 volts/km
The electric fields cause GICs to flow in the high voltage transmission grid
The induced voltages that drive the GICs can be modeled as dc voltages in the transmission lines.
  The magnitude of the dc voltage is determined by integrating the electric field variation over the line length
  Both magnitude and direction of electric field is important
33

## Slide 35: HILF Example: Nuclear EMPs
Broadly defined, an electromagnetic pulse (EMP) is any transient burst of electromagnetic energy
High altitude nuclear explosions can produce continental scale EMPs; called HEMPs
The impacts of an HEMP are typically divided into three time frames: E1, E2 and E3
  E1 impacts electronics, E2 is similar to lightning, E3 is similar to a very large, but short duration GMD

## Slide 36: Nuclear EMP History
The presence of EMPs was theorized by Enrico Fermi prior to the first explosion in July 1945
  Many wires were shielded, but still some data was lost due to EMP
British called it “radioflash” in their tests in early 1950’s due to the presence of “clicks” heard on radios
Operation Hardtack tests in 1958 (up to 80 km inaltitude) further demonstrated HEMP impacts
Trinity Explosion, July 16, 1945, 20 kilotons of TNT source: Los Alamos Lab

## Slide 37: Nuclear EMP History: Starfish Prime
Starfish Prime was an explosion of a 1.44 megaton nuclear weapon at an altitude of 400 km over the Pacific Ocean in July 1962
  Part of series of tests known as Operation Fishbowl
  The EMPs were much larger than expected, driving instruments off scale
  Impacts seen in Honolulu (1445 km away), including knocking out about 300 street lights, setting off alarms, and damaging a microwave link
  Some low earth orbit satellites were also damaged
Starfish Prime was an explosion of a 1.44 megaton nuclear weapon at an altitude of 400 km over the Pacific Ocean in July 1962
  Part of series of tests known as Operation Fishbowl
  The EMPs were much larger than expected, driving instruments off scale
  Impacts seen in Honolulu (1445 km away), including knocking out about 300 street lights, setting off alarms, and damaging a microwave link
  Some low earth orbit satellites were also damaged
Starfish Prime observed on Maui in 1962, Source US EMP Commission Report from July 2017

## Slide 38: Geomagnetically Induced Currents (GICs)
Both GMDs and HEMPs cause electric fields, with values dependent on the deep earth conductivity
Along length of a high voltage transmission line, electric fields can be modeled as a dc voltage source superimposed on the lines
These voltage sources produce quasi-dc geomagnetically induced currents (GICs) that are superimposed on the ac (60 Hz) flows
37

## Slide 39: Simulated GICs in High Voltage Transmission Grid

## Slide 40: The Impact of a Large GMD From an Operations Perspective
Would be maybe a day warning but without specifics
  Satellite at Lagrange point one million miles from earth would give more details, but with less than 30 minutes lead time
  Could strike quickly; rise time of minutes, rapidly covering a good chunk of the continent
Reactive power loadings on hundreds of high voltage transformers could rapidly rise
Increased transformer reactive loading causes heating issues and potential large-scale voltage collapses
Control room personnel would be overwhelmed
The storm could last for days with varying intensity
39

## Slide 41: GIC Mitigation
Tools are needed to determine mitigation strategies
  Cost-benefit analysis
GIC flows can be reduced both through operational strategies such as opening lines, and through longer term approaches such as installing blocking devices
Redispatching the system can change transformer loadings, providing margins for GICs
Algorithms are needed to provide real-time situational awareness for use during GMDs
40

## Slide 42: Integrating Weather (and Other Resiliency Events) into Electric gird Planning
Human activity depends on the weather, and this has always been reflected in the electric load
Traditionally some power flow parameters have depended on the weather (e.g., line ratings, turbine max MW, line resistance)
Over the last several decades this dependence has grown substantially with the increase in wind and solar generation
  They now provide about 17% of US electric energy (> 30% in ERCOT); there are times when most of the electricity in regions is supplied by these sources
  They are extremely dependent on the weather
Major power system input parameters are now heavily weather dependent (e.g., wind and solar generator Max MW)

## Slide 43: Using Weather and Related Data in the Power System Resiliency Studies
To use weather data and other environmental inputs (ENIs) in the power grids studies requires
  The availability of geographic information mapping buses to substations, and then geocoordinates for the substations
    This is now mostly available for North American grids
    Large-scale synthetic grids with geographic information are also available
  Convenient access to available to weather informationover the footprint of interest
    For planning often the footprint is large, beyond a single utility
  The availability of models that represent the impact of weather and other ENIs on electric grid components

## Slide 44: Availability of Weather Information
We started this effort three years back by using historical weather station measurements (mostly identified by their ICAOs [International Civil Aviation Organization], e.g. KLIT, KCLL)
  We had lots of data, but much of it had missing values; we also only had surface wind values and no direct solar measurements
  Such measurements at specific locations can still be very useful (e.g., at electrical substations)
There are many other sources of free weather information, with good coverage provided by Weather DataSet Needs for Planning and Analyzing Modern Power Systems, Energy Systems Integration Group (ESIG), October 2023
  www.esig.energy/wp-content/uploads/2023/10/ESIG-Weather-Datasets-summary-report-2023.pdf

## Slide 45: ESIG Report (10/2023)
“These widespread changes lead to the increasing weather-dependence of supply and demand, making power system planning dramatically more complex and requiring much more comprehensive weather data for robust system planning.”
“The work required to achieve a long-term solution to weather data needs is not trivial, but it is manageable and is much less costly than blindly building trillions of dollars of infrastructure without the basic tools to cost effectively optimize it and assess its reliability.”
PowerWorld had started working in planning weather integration about a year before the ESIG report appeared, but much progress has been made in the last year

## Slide 46: Weather Resiliencey Example: Renewable Resource Droughts
With the rapid growth in wind and solar resources, a growing concern is how to handle wind and solar “droughts” with the generic term of renewable resource droughts used to describe them
The below example is a wind drought that occurred in the Midwest in late January 2020

## Slide 47: HICSS 2025 Paper on Power Flow Weather Modeling
There is a paper from the 59th Hawaii International Conference on System Sciences (HICSS) titled, “Power Flow Modeling of the Impacts of Weather and Other Resiliency Hazards With a Focus on Transmission Planning,”; it is available at overbye.engr.tamu.edu/publications

## Slide 48: Strategies to Prepare For and Mitigate Large- Area, Long-Duration Blackouts
While events may vary, there a number of broad approaches that can be used to help improve resilience
Image Source: Figure 4.1, NAS, 2017

## Slide 49: Component Hardening, Physical Security
Electric grids are comprised of components, and resiliency can be enhanced by hardening particularly vulnerable components
  Transmission lines in likely icing location, undergrounding some lines, transformers with better handling of geomagnetically induced currents (GICs), water protection
  This needs to be done considering the cost versus benefit
  Vegetation management should also be considered
Physical security is an area of increased concern, with unmanned aerial vehicles being a fast rising threat

## Slide 50: Enhancing Bulk Grid Simulations to Handle HILF Scenarios
The stressed operation associated with the high impact, low frequency events presents modeling challenges
Luckily, over the last several years the software is being enhanced to deal with these situations
  My next presentation goes in-depth on geomagnetic disturbance (GMD) and high altitude electromagnetic pulse (HEMP) modeling
There is also a need to consider high voltage transmission system design that lessens the likelihood of cascading outages

## Slide 51: Adaptive Islanding
One promising resiliency technique is to design interconnected grids to split (island)
  This is known as controlled islanding and can be enhanced to be adaptive islanding
  A distribution system example is a microgrid
The islands need to be chosen so they have sufficient generation to match load
Often control is still centralized
A more involved islanding issue is to setup the grid so smaller parts can function with full autonomy

## Slide 52: Resiliency and Coupled Infrastructures
As our societies become more dependent on electricity, short and small duration blackouts become more concerning, and large-scale, long duration outages can be catastrophic
There are many couplings between electric grids and other infrastructures such as natural gas, water, cyber, and increasing transportation
These couples need to be more fully considered in electric grid resiliency modeling and simulation

## Slide 53: Some Specific Recommendations to Enhance Resilience
A “visioning” process is needed to imaging and assessing plausible high impact events
The electric grid operators need to do exercises to better simulate high impact scenarios
More physical components are needed, including replacement transformers and backup power
More research, development and demonstration is needed, including a focus on cyber and HILFs
Resilience groups are needed throughout the industry and government to raise awareness
Source: National Academies 2017 “Enhancing the Resilience of the Nation’s Electricity System”
52

## Slide 54: Porting PowerWorld Simulator to Linux
Simulator was started in 1990s as a Windows only program. It’s design and implementation reflect that.
  Simulator has an object-oriented design
  Simulator makes use of windows specific (WinAPI) features
  Uses Delphi forms library (VCL)
  In some cases the computational code and the code to support the GUI are in the same unit (file)
    This makes perfect sense in Windows, but it means you can’t create the object without also creating the form.
    To compile in Linux, these must be separated
    This is relatively straight forward, but scoping can be an issue because in Delphi everything is in scope within a unit
Goal is to port at least key parts of the computational capabilities to Linux

## Slide 55: Conclusion and Questions?
The electric grid is crucial to societies worldwide, and for decades into the future we will be relying on it
A perfect electric grid is impossible, and we need to be prepared for long-term, wide-area blackouts
However, much can and should be done to reduce to reduce this risk
A broad, sustained effort is needed in this area including the entire electric grid sector
Synthetic electric grids will play a crucial role in this effort
54

## Slide 56: Thank You! Questions?